## Hall
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | RS Logic | Nota | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec | PLC IP
1 | FC-614-01/02/03/04 pt100 input 1 | UA | Hall-52C | HVAC | PT100-FC1 | 1 | Temperature | Mon | UA-Hall-52C:HVAC-PT100-FC1-1:Temperature-Mon | TEAMB01_ST_614_01_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_01_1.val | .1 | 5
2 | FC-614-01/02/03/04 pt100 input 2 | UA | Hall-54C | HVAC | PT100-FC1 | 2 | Temperature | Mon | UA-Hall-54C:HVAC-PT100-FC1-2:Temperature-Mon | TEAMB02_ST_614_01_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_01_2.val | .1 | 5
3 | FC-614-01/02/03/04 pt100 input 3 | UA | Hall-55C | HVAC | PT100-FC1 | 3 | Temperature | Mon | UA-Hall-55C:HVAC-PT100-FC1-3:Temperature-Mon | TEAMB03_ST_614_01_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_01_3.val | .1 | 5
4 | FC-614-01/02/03/04 pt100 input 4 | UA | Hall-56C | HVAC | PT100-FC1 | 4 | Temperature | Mon | UA-Hall-56C:HVAC-PT100-FC1-4:Temperature-Mon | TEAMB04_ST_614_01_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_01_4.val | .1 | 5
5 | FC-614-01/02/03/04 pt100 input 5 | UA | Hall-53B | HVAC | PT100-FC1 | 5 | Temperature | Mon | UA-Hall-53B:HVAC-PT100-FC1-5:Temperature-Mon | TEAMB05_ST_614_01_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_01_5.val | .1 | 5
6 | FC-614-01/02/03/04 pt100 input 6 | UA | Hall-57B | HVAC | PT100-FC1 | 6 | Temperature | Mon | UA-Hall-57B:HVAC-PT100-FC1-6:Temperature-Mon | TEAMB06_ST_614_01_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_01_6.val | .1 | 5
7 | FC-614-01/02/03/04 pt100 input 7 | UA | Hall-52D | HVAC | PT100-FC1 | 7 | Temperature | Mon | UA-Hall-52D:HVAC-PT100-FC1-7:Temperature-Mon | TEAMB07_ST_614_01_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_01_7.val | .1 | 5
8 | FC-614-01/02/03/04 pt100 input 8 | UA | Hall-55D | HVAC | PT100-FC2 | 8 | Temperature | Mon | UA-Hall-55D:HVAC-PT100-FC2-8:Temperature-Mon | TEAMB08_ST_614_01_8.val |  | Analog | Input |  |  | C | TEAMB08_ST_614_01_8.val | .1 | 5
9 | FC-614-06/07/08/09 pt100 input 1 | UA | Hall-58C | HVAC | PT100-FC2 | 1 | Temperature | Mon | UA-Hall-58C:HVAC-PT100-FC2-1:Temperature-Mon | TEAMB01_ST_614_03_1.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB01_ST_614_03_1.val | .1 | 5
10 | FC-614-06/07/08/09 pt100 input 2 | UA | Hall-60C | HVAC | PT100-FC2 | 2 | Temperature | Mon | UA-Hall-60C:HVAC-PT100-FC2-2:Temperature-Mon | TEAMB02_ST_614_03_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_03_2.val | .1 | 5
11 | FC-614-06/07/08/09 pt100 input 3 | UA | Hall-01C | HVAC | PT100-FC2 | 3 | Temperature | Mon | UA-Hall-01C:HVAC-PT100-FC2-3:Temperature-Mon | TEAMB03_ST_614_03_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_03_3.val | .1 | 5
12 | FC-614-06/07/08/09 pt100 input 4 | UA | Hall-02C | HVAC | PT100-FC2 | 4 | Temperature | Mon | UA-Hall-02C:HVAC-PT100-FC2-4:Temperature-Mon | TEAMB04_ST_614_03_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_03_4.val | .1 | 5
13 | FC-614-06/07/08/09 pt100 input 5 | UA | Hall-03B | HVAC | PT100-FC2 | 5 | Temperature | Mon | UA-Hall-03B:HVAC-PT100-FC2-5:Temperature-Mon | TEAMB05_ST_614_03_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_03_5.val | .1 | 5
14 | FC-614-06/07/08/09 pt100 input 6 | UA | Hall-58D | HVAC | PT100-FC2 | 6 | Temperature | Mon | UA-Hall-58D:HVAC-PT100-FC2-6:Temperature-Mon | TEAMB06_ST_614_03_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_03_6.val | .1 | 5
15 | FC-614-06/07/08/09 pt100 input 7 | UA | Hall-58D | HVAC | PT100-FC2 | 7 | Temperature | Mon | UA-Hall-58D:HVAC-PT100-FC2-7:Temperature-Mon | TEAMB07_ST_614_03_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_03_7.val | .1 | 5
16 | FC-614-06/07/08/09 pt100 input 8 | UA | - | HVAC | PT100-FC2 | 8 | Temperature | Mon | UA--:HVAC-PT100-FC2-8:Temperature-Mon | TEAMB08_ST_614_03_8.val | Inibido - BMS não lê | Analog | Input |  |  | C | TEAMB08_ST_614_03_8.val | .1 | 5
17 | FC-614-11/12/13/14 pt100 input 1 | UA | Hall-04C | HVAC | PT100-FC3 | 1 | Temperature | Mon | UA-Hall-04C:HVAC-PT100-FC3-1:Temperature-Mon | TEAMB01_ST_614_05_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_05_1.val | .1 | 5
18 | FC-614-11/12/13/14 pt100 input 2 | UA | Hall-05C | HVAC | PT100-FC3 | 2 | Temperature | Mon | UA-Hall-05C:HVAC-PT100-FC3-2:Temperature-Mon | TEAMB02_ST_614_05_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_05_2.val | .1 | 5
19 | FC-614-11/12/13/14 pt100 input 3 | UA | Hall-07C | HVAC | PT100-FC3 | 3 | Temperature | Mon | UA-Hall-07C:HVAC-PT100-FC3-3:Temperature-Mon | TEAMB03_ST_614_05_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_05_3.val | .1 | 5
20 | FC-614-11/12/13/14 pt100 input 4 | UA | Hall-08C | HVAC | PT100-FC3 | 4 | Temperature | Mon | UA-Hall-08C:HVAC-PT100-FC3-4:Temperature-Mon | TEAMB04_ST_614_05_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_05_4.val | .1 | 5
21 | FC-614-11/12/13/14 pt100 input 5 | UA | Halll-06B | HVAC | PT100-FC3 | 5 | Temperature | Mon | UA-Halll-06B:HVAC-PT100-FC3-5:Temperature-Mon | TEAMB05_ST_614_05_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_05_5.val | .1 | 5
22 | FC-614-11/12/13/14 pt100 input 6 | UA | Hall-08B | HVAC | PT100-FC3 | 6 | Temperature | Mon | UA-Hall-08B:HVAC-PT100-FC3-6:Temperature-Mon | TEAMB06_ST_614_05_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_05_6.val | .1 | 5
23 | FC-614-11/12/13/14 pt100 input 7 | UA | Hall-04D | HVAC | PT100-FC3 | 7 | Temperature | Mon | UA-Hall-04D:HVAC-PT100-FC3-7:Temperature-Mon | TEAMB07_ST_614_05_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_05_7.val | .1 | 5
24 | FC-614-11/12/13/14 pt100 input 8 | UA | Hall-07D | HVAC | PT100-FC3 | 8 | Temperature | Mon | UA-Hall-07D:HVAC-PT100-FC3-8:Temperature-Mon | TEAMB08_ST_614_05_8.val |  | Analog | Input |  |  | C | TEAMB08_ST_614_05_8.val | .1 | 5
25 | FC-614-16/17/18/19 pt100 input 1 | UA | Hall-10B | HVAC | PT100-FC4 | 1 | Temperature | Mon | UA-Hall-10B:HVAC-PT100-FC4-1:Temperature-Mon | TEAMB01_ST_614_07_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_07_1.val | .1 | 5
26 | FC-614-16/17/18/19 pt100 input 2 | UA | Hall-11B | HVAC | PT100-FC4 | 2 | Temperature | Mon | UA-Hall-11B:HVAC-PT100-FC4-2:Temperature-Mon | TEAMB02_ST_614_07_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_07_2.val | .1 | 5
27 | FC-614-16/17/18/19 pt100 input 3 | UA | Hall-13B | HVAC | PT100-FC4 | 3 | Temperature | Mon | UA-Hall-13B:HVAC-PT100-FC4-3:Temperature-Mon | TEAMB03_ST_614_07_3.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB03_ST_614_07_3.val | .1 | 5
28 | FC-614-16/17/18/19 pt100 input 4 | UA | Hall-13C | HVAC | PT100-FC4 | 4 | Temperature | Mon | UA-Hall-13C:HVAC-PT100-FC4-4:Temperature-Mon | TEAMB04_ST_614_07_4.val | Corrigir localização | Analog | Input |  |  | C | TEAMB04_ST_614_07_4.val | .1 | 5
29 | FC-614-16/17/18/19 pt100 input 5 | UA | Hall-15C | HVAC | PT100-FC4 | 5 | Temperature | Mon | UA-Hall-15C:HVAC-PT100-FC4-5:Temperature-Mon | TEAMB05_ST_614_07_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_07_5.val | .1 | 5
30 | FC-614-16/17/18/19 pt100 input 6 | UA | Hall-12C | HVAC | PT100-FC4 | 6 | Temperature | Mon | UA-Hall-12C:HVAC-PT100-FC4-6:Temperature-Mon | TEAMB06_ST_614_07_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_07_6.val | .1 | 5
31 | FC-614-16/17/18/19 pt100 input 7 | UA | Hall-10D | HVAC | PT100-FC4 | 7 | Temperature | Mon | UA-Hall-10D:HVAC-PT100-FC4-7:Temperature-Mon | TEAMB07_ST_614_07_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_07_7.val | .1 | 5
32 | FC-614-16/17/18/19 pt100 input 8 | UA | Hall-13D | HVAC | PT100-FC4 | 8 | Temperature | Mon | UA-Hall-13D:HVAC-PT100-FC4-8:Temperature-Mon | TEAMB08_ST_614_07_8.val |  | Analog | Input |  |  | C | TEAMB08_ST_614_07_8.val | .1 | 5
33 | FC-614-21/22/23/24 pt100 input 1 | UA | Hall-15C | HVAC | PT100-FC5 | 1 | Temperature | Mon | UA-Hall-15C:HVAC-PT100-FC5-1:Temperature-Mon | TEAMB01_ST_614_09_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_09_1.val | .1 | 5
34 | FC-614-21/22/23/24 pt100 input 2 | UA | Hall-17C | HVAC | PT100-FC5 | 2 | Temperature | Mon | UA-Hall-17C:HVAC-PT100-FC5-2:Temperature-Mon | TEAMB02_ST_614_09_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_09_2.val | .1 | 5
35 | FC-614-21/22/23/24 pt100 input 3 | UA | Hall-19C | HVAC | PT100-FC5 | 3 | Temperature | Mon | UA-Hall-19C:HVAC-PT100-FC5-3:Temperature-Mon | TEAMB03_ST_614_09_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_09_3.val | .1 | 5
36 | FC-614-21/22/23/24 pt100 input 4 | UA | Hall-20C | HVAC | PT100-FC5 | 4 | Temperature | Mon | UA-Hall-20C:HVAC-PT100-FC5-4:Temperature-Mon | TEAMB04_ST_614_09_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_09_4.val | .1 | 5
37 | FC-614-21/22/23/24 pt100 input 5 | UA | Hall-17B | HVAC | PT100-FC5 | 5 | Temperature | Mon | UA-Hall-17B:HVAC-PT100-FC5-5:Temperature-Mon | TEAMB05_ST_614_09_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_09_5.val | .1 | 5
38 | FC-614-21/22/23/24 pt100 input 6 | UA | Hall-21B | HVAC | PT100-FC5 | 6 | Temperature | Mon | UA-Hall-21B:HVAC-PT100-FC5-6:Temperature-Mon | TEAMB06_ST_614_09_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_09_6.val | .1 | 5
39 | FC-614-21/22/23/24 pt100 input 7 | UA | Hall-19D | HVAC | PT100-FC5 | 7 | Temperature | Mon | UA-Hall-19D:HVAC-PT100-FC5-7:Temperature-Mon | TEAMB07_ST_614_09_7.val | Inibido - cartão em falha & Corrigir localização | Analog | Input |  |  | C | TEAMB07_ST_614_09_7.val | .1 | 5
40 | FC-614-21/22/23/24 pt100 input 8 | UA | Hall-16D | HVAC | PT100-FC5 | 8 | Temperature | Mon | UA-Hall-16D:HVAC-PT100-FC5-8:Temperature-Mon | TEAMB08_ST_614_09_8.val | Inibido - cartão em falha & Corrigir localização | Analog | Input |  |  | C | TEAMB08_ST_614_09_8.val | .1 | 5
41 | FC-614-26/27/28/29 pt100 input 1 | UA | Hall-22C | HVAC | PT100-FC6 | 1 | Temperature | Mon | UA-Hall-22C:HVAC-PT100-FC6-1:Temperature-Mon | TEAMB01_ST_614_11_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_11_1.val | .1 | 5
42 | FC-614-26/27/28/29 pt100 input 2 | UA | Hall-24C | HVAC | PT100-FC6 | 2 | Temperature | Mon | UA-Hall-24C:HVAC-PT100-FC6-2:Temperature-Mon | TEAMB02_ST_614_11_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_11_2.val | .1 | 5
43 | FC-614-26/27/28/29 pt100 input 3 | UA | Hall-25C | HVAC | PT100-FC6 | 3 | Temperature | Mon | UA-Hall-25C:HVAC-PT100-FC6-3:Temperature-Mon | TEAMB03_ST_614_11_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_11_3.val | .1 | 5
44 | FC-614-26/27/28/29 pt100 input 4 | UA | Hall-26C | HVAC | PT100-FC6 | 4 | Temperature | Mon | UA-Hall-26C:HVAC-PT100-FC6-4:Temperature-Mon | TEAMB04_ST_614_11_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_11_4.val | .1 | 5
45 | FC-614-26/27/28/29 pt100 input 5 | UA | No-loca | HVAC | PT100-FC6 | 5 | Temperature | Mon | UA-No-loca:HVAC-PT100-FC6-5:Temperature-Mon | TEAMB05_ST_614_11_5.val | AS-BUILT (NO FC) BMS 25° | Analog | Input |  |  | C | TEAMB05_ST_614_11_5.val | .1 | 5
46 | FC-614-26/27/28/29 pt100 input 6 | UA | No-loca | HVAC | PT100-FC6 | 6 | Temperature | Mon | UA-No-loca:HVAC-PT100-FC6-6:Temperature-Mon | TEAMB06_ST_614_11_6.val | AS-BUILT (NO FC) BMS 25° | Analog | Input |  |  | C | TEAMB06_ST_614_11_6.val | .1 | 5
47 | FC-614-26/27/28/29 pt100 input 7 | UA | Hall-22D | HVAC | PT100-FC6 | 7 | Temperature | Mon | UA-Hall-22D:HVAC-PT100-FC6-7:Temperature-Mon | TEAMB07_ST_614_11_7.val | AS-BUILT (NO FC) BMS 25° | Analog | Input |  |  | C | TEAMB07_ST_614_11_7.val | .1 | 5
48 | FC-614-26/27/28/29 pt100 input 8 | UA | Hall-25D | HVAC | PT100-FC6 | 8 | Temperature | Mon | UA-Hall-25D:HVAC-PT100-FC6-8:Temperature-Mon | TEAMB08_ST_614_11_8.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB08_ST_614_11_8.val | .1 | 5
49 | FC-614-32/33/34/35 pt100 input 1 | UA | Hall-32C | HVAC | PT100-FC7 | 1 | Temperature | Mon | UA-Hall-32C:HVAC-PT100-FC7-1:Temperature-Mon | TEAMB01_ST_614_13_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_13_1.val | .1 | 5
50 | FC-614-32/33/34/35 pt100 input 2 | UA | Hall-31C | HVAC | PT100-FC7 | 2 | Temperature | Mon | UA-Hall-31C:HVAC-PT100-FC7-2:Temperature-Mon | TEAMB02_ST_614_13_2.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB02_ST_614_13_2.val | .1 | 5
51 | FC-614-32/33/34/35 pt100 input 3 | UA | Hall-29C | HVAC | PT100-FC7 | 3 | Temperature | Mon | UA-Hall-29C:HVAC-PT100-FC7-3:Temperature-Mon | TEAMB03_ST_614_13_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_13_3.val | .1 | 5
52 | FC-614-32/33/34/35 pt100 input 4 | UA | Hall-28C | HVAC | PT100-FC7 | 4 | Temperature | Mon | UA-Hall-28C:HVAC-PT100-FC7-4:Temperature-Mon | TEAMB04_ST_614_13_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_13_4.val | .1 | 5
53 | FC-614-32/33/34/35 pt100 input 5 | UA | Hall-29B | HVAC | PT100-FC7 | 5 | Temperature | Mon | UA-Hall-29B:HVAC-PT100-FC7-5:Temperature-Mon | TEAMB05_ST_614_13_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_13_5.val | .1 | 5
54 | FC-614-32/33/34/35 pt100 input 6 | UA | Hall-32B | HVAC | PT100-FC7 | 6 | Temperature | Mon | UA-Hall-32B:HVAC-PT100-FC7-6:Temperature-Mon | TEAMB06_ST_614_13_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_13_6.val | .1 | 5
55 | FC-614-32/33/34/35 pt100 input 7 | UA | Hall-28D | HVAC | PT100-FC7 | 7 | Temperature | Mon | UA-Hall-28D:HVAC-PT100-FC7-7:Temperature-Mon | TEAMB07_ST_614_13_7.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB07_ST_614_13_7.val | .1 | 5
56 | FC-614-32/33/34/35 pt100 input 8 | UA | Hall-31D | HVAC | PT100-FC7 | 8 | Temperature | Mon | UA-Hall-31D:HVAC-PT100-FC7-8:Temperature-Mon | TEAMB08_ST_614_13_8.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB08_ST_614_13_8.val | .1 | 5
57 | FC-614-37/38/39/40 pt100 input 1 | UA | Hall-33C | HVAC | PT100-FC8 | 1 | Temperature | Mon | UA-Hall-33C:HVAC-PT100-FC8-1:Temperature-Mon | TEAMB01_ST_614_15_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_15_1.val | .1 | 5
58 | FC-614-37/38/39/40 pt100 input 2 | UA | Hall-35C | HVAC | PT100-FC8 | 2 | Temperature | Mon | UA-Hall-35C:HVAC-PT100-FC8-2:Temperature-Mon | TEAMB02_ST_614_15_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_15_2.val | .1 | 5
59 | FC-614-37/38/39/40 pt100 input 3 | UA | Hall-37C | HVAC | PT100-FC8 | 3 | Temperature | Mon | UA-Hall-37C:HVAC-PT100-FC8-3:Temperature-Mon | TEAMB03_ST_614_15_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_15_3.val | .1 | 5
60 | FC-614-37/38/39/40 pt100 input 4 | UA | Hall-38C | HVAC | PT100-FC8 | 4 | Temperature | Mon | UA-Hall-38C:HVAC-PT100-FC8-4:Temperature-Mon | TEAMB04_ST_614_15_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_15_4.val | .1 | 5
61 | FC-614-37/38/39/40 pt100 input 5 | UA | Hall-34B | HVAC | PT100-FC8 | 5 | Temperature | Mon | UA-Hall-34B:HVAC-PT100-FC8-5:Temperature-Mon | TEAMB05_ST_614_15_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_15_5.val | .1 | 5
62 | FC-614-37/38/39/40 pt100 input 6 | UA | Hall-40B | HVAC | PT100-FC8 | 6 | Temperature | Mon | UA-Hall-40B:HVAC-PT100-FC8-6:Temperature-Mon | TEAMB06_ST_614_15_6.val | Inibido - mau contato & corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_15_6.val | .1 | 5
63 | FC-614-37/38/39/40 pt100 input 7 | UA | Hall-34D | HVAC | PT100-FC8 | 7 | Temperature | Mon | UA-Hall-34D:HVAC-PT100-FC8-7:Temperature-Mon | TEAMB07_ST_614_15_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_15_7.val | .1 | 5
64 | FC-614-37/38/39/40 pt100 input 8 | UA | Hall-37D | HVAC | PT100-FC8 | 8 | Temperature | Mon | UA-Hall-37D:HVAC-PT100-FC8-8:Temperature-Mon | TEAMB08_ST_614_15_8.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB08_ST_614_15_8.val | .1 | 5
65 | FC-614-42/43/44/45 input 1 | UA | Hall-44C | HVAC | PT100-FC9 | 1 | Temperature | Mon | UA-Hall-44C:HVAC-PT100-FC9-1:Temperature-Mon | TEAMB01_ST_614_18_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_18_1.val | .1 | 5
66 | FC-614-42/43/44/45 input 2 | UA | Hall-43C | HVAC | PT100-FC9 | 2 | Temperature | Mon | UA-Hall-43C:HVAC-PT100-FC9-2:Temperature-Mon | TEAMB02_ST_614_18_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_18_2.val | .1 | 5
67 | FC-614-42/43/44/45 input 3 | UA | Hall-41C | HVAC | PT100-FC9 | 3 | Temperature | Mon | UA-Hall-41C:HVAC-PT100-FC9-3:Temperature-Mon | TEAMB03_ST_614_18_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_18_3.val | .1 | 5
68 | FC-614-42/43/44/45 input 4 | UA | Hall-40C | HVAC | PT100-FC9 | 4 | Temperature | Mon | UA-Hall-40C:HVAC-PT100-FC9-4:Temperature-Mon | TEAMB04_ST_614_18_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_18_4.val | .1 | 5
69 | FC-614-42/43/44/45 input 5 | UA | Hall-43B | HVAC | PT100-FC9 | 5 | Temperature | Mon | UA-Hall-43B:HVAC-PT100-FC9-5:Temperature-Mon | TEAMB05_ST_614_18_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_18_5.val | .1 | 5
70 | FC-614-42/43/44/45 input 6 | UA | Hall-41B | HVAC | PT100-FC9 | 6 | Temperature | Mon | UA-Hall-41B:HVAC-PT100-FC9-6:Temperature-Mon | TEAMB06_ST_614_18_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_18_6.val | .1 | 5
71 | FC-614-42/43/44/45 input 7 | UA | Hall-40D | HVAC | PT100-FC9 | 7 | Temperature | Mon | UA-Hall-40D:HVAC-PT100-FC9-7:Temperature-Mon | TEAMB07_ST_614_18_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_18_7.val | .1 | 5
72 | FC-614-42/43/44/45 input 8 | UA | Hall-43D | HVAC | PT100-FC9 | 8 | Temperature | Mon | UA-Hall-43D:HVAC-PT100-FC9-8:Temperature-Mon | TEAMB08_ST_614_18_8.val |  | Analog | Input |  |  | C | TEAMB08_ST_614_18_8.val | .1 | 5
73 | FC-614-47/48/49/50 pt100 input 1 | UA | Hall-51C | HVAC | PT100-FC10 | 1 | Temperature | Mon | UA-Hall-51C:HVAC-PT100-FC10-1:Temperature-Mon | TEAMB01_ST_614_20_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_20_1.val | .1 | 5
74 | FC-614-47/48/49/50 pt100 input 2 | UA | Hall-49C | HVAC | PT100-FC10 | 2 | Temperature | Mon | UA-Hall-49C:HVAC-PT100-FC10-2:Temperature-Mon | TEAMB02_ST_614_20_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_20_2.val | .1 | 5
75 | FC-614-47/48/49/50 pt100 input 3 | UA | Hall-47C | HVAC | PT100-FC10 | 3 | Temperature | Mon | UA-Hall-47C:HVAC-PT100-FC10-3:Temperature-Mon | TEAMB03_ST_614_20_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_20_3.val | .1 | 5
76 | FC-614-47/48/49/50 pt100 input 4 | UA | Hall-46C | HVAC | PT100-FC10 | 4 | Temperature | Mon | UA-Hall-46C:HVAC-PT100-FC10-4:Temperature-Mon | TEAMB04_ST_614_20_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_20_4.val | .1 | 5
77 | FC-614-47/48/49/50 pt100 input 5 | UA | Hall-47B | HVAC | PT100-FC10 | 5 | Temperature | Mon | UA-Hall-47B:HVAC-PT100-FC10-5:Temperature-Mon | TEAMB05_ST_614_20_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_20_5.val | .1 | 5
78 | FC-614-47/48/49/50 pt100 input 6 | UA | Hall-50B | HVAC | PT100-FC10 | 6 | Temperature | Mon | UA-Hall-50B:HVAC-PT100-FC10-6:Temperature-Mon | TEAMB06_ST_614_20_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_20_6.val | .1 | 5
79 | FC-614-47/48/49/50 pt100 input 7 | UA | Hall-46D | HVAC | PT100-FC10 | 7 | Temperature | Mon | UA-Hall-46D:HVAC-PT100-FC10-7:Temperature-Mon | TEAMB07_ST_614_20_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_20_7.val | .1 | 5
80 | FC-614-47/48/49/50 pt100 input 8 | UA | Hall-49D | HVAC | PT100-FC10 | 8 | Temperature | Mon | UA-Hall-49D:HVAC-PT100-FC10-8:Temperature-Mon | TEAMB08_ST_614_20_8.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB08_ST_614_20_8.val | .1 | 5

## plc1
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | RS Logic | Nota | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec | PLC IP
1 | FC-614-01/02/03/04 pt100 input 1 | UA | Hall-52C | HVAC | PT100-FC1 | 1 | Temperature | Mon | UA-Hall-52C:HVAC-PT100-FC1-1:Temperature-Mon | TEAMB01_ST_614_01_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_01_1.val | .1
2 | FC-614-01/02/03/04 pt100 input 2 | UA | Hall-54C | HVAC | PT100-FC1 | 2 | Temperature | Mon | UA-Hall-54C:HVAC-PT100-FC1-2:Temperature-Mon | TEAMB02_ST_614_01_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_01_2.val | .1
3 | FC-614-01/02/03/04 pt100 input 3 | UA | Hall-55C | HVAC | PT100-FC1 | 3 | Temperature | Mon | UA-Hall-55C:HVAC-PT100-FC1-3:Temperature-Mon | TEAMB03_ST_614_01_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_01_3.val | .1
4 | FC-614-01/02/03/04 pt100 input 4 | UA | Hall-56C | HVAC | PT100-FC1 | 4 | Temperature | Mon | UA-Hall-56C:HVAC-PT100-FC1-4:Temperature-Mon | TEAMB04_ST_614_01_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_01_4.val | .1
5 | FC-614-01/02/03/04 pt100 input 5 | UA | Hall-53B | HVAC | PT100-FC1 | 5 | Temperature | Mon | UA-Hall-53B:HVAC-PT100-FC1-5:Temperature-Mon | TEAMB05_ST_614_01_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_01_5.val | .1
6 | FC-614-01/02/03/04 pt100 input 6 | UA | Hall-57B | HVAC | PT100-FC1 | 6 | Temperature | Mon | UA-Hall-57B:HVAC-PT100-FC1-6:Temperature-Mon | TEAMB06_ST_614_01_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_01_6.val | .1
7 | FC-614-01/02/03/04 pt100 input 7 | UA | Hall-52D | HVAC | PT100-FC1 | 7 | Temperature | Mon | UA-Hall-52D:HVAC-PT100-FC1-7:Temperature-Mon | TEAMB07_ST_614_01_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_01_7.val | .1
8 | FC-614-01/02/03/04 pt100 input 8 | UA | Hall-55D | HVAC | PT100-FC2 | 8 | Temperature | Mon | UA-Hall-55D:HVAC-PT100-FC2-8:Temperature-Mon | TEAMB08_ST_614_01_8.val |  | Analog | Input |  |  | C | TEAMB08_ST_614_01_8.val | .1
65 | FC-614-42/43/44/45 input 1 | UA | Hall-44C | HVAC | PT100-FC9 | 1 | Temperature | Mon | UA-Hall-44C:HVAC-PT100-FC9-1:Temperature-Mon | TEAMB01_ST_614_18_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_18_1.val | .1
66 | FC-614-42/43/44/45 input 2 | UA | Hall-43C | HVAC | PT100-FC9 | 2 | Temperature | Mon | UA-Hall-43C:HVAC-PT100-FC9-2:Temperature-Mon | TEAMB02_ST_614_18_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_18_2.val | .1
67 | FC-614-42/43/44/45 input 3 | UA | Hall-41C | HVAC | PT100-FC9 | 3 | Temperature | Mon | UA-Hall-41C:HVAC-PT100-FC9-3:Temperature-Mon | TEAMB03_ST_614_18_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_18_3.val | .1
68 | FC-614-42/43/44/45 input 4 | UA | Hall-40C | HVAC | PT100-FC9 | 4 | Temperature | Mon | UA-Hall-40C:HVAC-PT100-FC9-4:Temperature-Mon | TEAMB04_ST_614_18_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_18_4.val | .1
69 | FC-614-42/43/44/45 input 5 | UA | Hall-43B | HVAC | PT100-FC9 | 5 | Temperature | Mon | UA-Hall-43B:HVAC-PT100-FC9-5:Temperature-Mon | TEAMB05_ST_614_18_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_18_5.val | .1
70 | FC-614-42/43/44/45 input 6 | UA | Hall-41B | HVAC | PT100-FC9 | 6 | Temperature | Mon | UA-Hall-41B:HVAC-PT100-FC9-6:Temperature-Mon | TEAMB06_ST_614_18_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_18_6.val | .1
71 | FC-614-42/43/44/45 input 7 | UA | Hall-40D | HVAC | PT100-FC9 | 7 | Temperature | Mon | UA-Hall-40D:HVAC-PT100-FC9-7:Temperature-Mon | TEAMB07_ST_614_18_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_18_7.val | .1
72 | FC-614-42/43/44/45 input 8 | UA | Hall-43D | HVAC | PT100-FC9 | 8 | Temperature | Mon | UA-Hall-43D:HVAC-PT100-FC9-8:Temperature-Mon | TEAMB08_ST_614_18_8.val |  | Analog | Input |  |  | C | TEAMB08_ST_614_18_8.val | .1
73 | FC-614-47/48/49/50 pt100 input 1 | UA | Hall-51C | HVAC | PT100-FC10 | 1 | Temperature | Mon | UA-Hall-51C:HVAC-PT100-FC10-1:Temperature-Mon | TEAMB01_ST_614_20_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_20_1.val | .1
74 | FC-614-47/48/49/50 pt100 input 2 | UA | Hall-49C | HVAC | PT100-FC10 | 2 | Temperature | Mon | UA-Hall-49C:HVAC-PT100-FC10-2:Temperature-Mon | TEAMB02_ST_614_20_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_20_2.val | .1
75 | FC-614-47/48/49/50 pt100 input 3 | UA | Hall-47C | HVAC | PT100-FC10 | 3 | Temperature | Mon | UA-Hall-47C:HVAC-PT100-FC10-3:Temperature-Mon | TEAMB03_ST_614_20_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_20_3.val | .1
76 | FC-614-47/48/49/50 pt100 input 4 | UA | Hall-46C | HVAC | PT100-FC10 | 4 | Temperature | Mon | UA-Hall-46C:HVAC-PT100-FC10-4:Temperature-Mon | TEAMB04_ST_614_20_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_20_4.val | .1
77 | FC-614-47/48/49/50 pt100 input 5 | UA | Hall-47B | HVAC | PT100-FC10 | 5 | Temperature | Mon | UA-Hall-47B:HVAC-PT100-FC10-5:Temperature-Mon | TEAMB05_ST_614_20_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_20_5.val | .1
78 | FC-614-47/48/49/50 pt100 input 6 | UA | Hall-50B | HVAC | PT100-FC10 | 6 | Temperature | Mon | UA-Hall-50B:HVAC-PT100-FC10-6:Temperature-Mon | TEAMB06_ST_614_20_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_20_6.val | .1
79 | FC-614-47/48/49/50 pt100 input 7 | UA | Hall-46D | HVAC | PT100-FC10 | 7 | Temperature | Mon | UA-Hall-46D:HVAC-PT100-FC10-7:Temperature-Mon | TEAMB07_ST_614_20_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_20_7.val | .1
80 | FC-614-47/48/49/50 pt100 input 8 | UA | Hall-49D | HVAC | PT100-FC10 | 8 | Temperature | Mon | UA-Hall-49D:HVAC-PT100-FC10-8:Temperature-Mon | TEAMB08_ST_614_20_8.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB08_ST_614_20_8.val | .1

## plc2
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | RS Logic | Nota | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec | PLC IP
9 | FC-614-06/07/08/09 pt100 input 1 | UA | Hall-58C | HVAC | PT100-FC2 | 1 | Temperature | Mon | UA-Hall-58C:HVAC-PT100-FC2-1:Temperature-Mon | TEAMB01_ST_614_03_1.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB01_ST_614_03_1.val | .1
10 | FC-614-06/07/08/09 pt100 input 2 | UA | Hall-60C | HVAC | PT100-FC2 | 2 | Temperature | Mon | UA-Hall-60C:HVAC-PT100-FC2-2:Temperature-Mon | TEAMB02_ST_614_03_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_03_2.val | .1
11 | FC-614-06/07/08/09 pt100 input 3 | UA | Hall-01C | HVAC | PT100-FC2 | 3 | Temperature | Mon | UA-Hall-01C:HVAC-PT100-FC2-3:Temperature-Mon | TEAMB03_ST_614_03_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_03_3.val | .1
12 | FC-614-06/07/08/09 pt100 input 4 | UA | Hall-02C | HVAC | PT100-FC2 | 4 | Temperature | Mon | UA-Hall-02C:HVAC-PT100-FC2-4:Temperature-Mon | TEAMB04_ST_614_03_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_03_4.val | .1
13 | FC-614-06/07/08/09 pt100 input 5 | UA | Hall-03B | HVAC | PT100-FC2 | 5 | Temperature | Mon | UA-Hall-03B:HVAC-PT100-FC2-5:Temperature-Mon | TEAMB05_ST_614_03_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_03_5.val | .1
14 | FC-614-06/07/08/09 pt100 input 6 | UA | Hall-58D | HVAC | PT100-FC2 | 6 | Temperature | Mon | UA-Hall-58D:HVAC-PT100-FC2-6:Temperature-Mon | TEAMB06_ST_614_03_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_03_6.val | .1
15 | FC-614-06/07/08/09 pt100 input 7 | UA | Hall-58D | HVAC | PT100-FC2 | 7 | Temperature | Mon | UA-Hall-58D:HVAC-PT100-FC2-7:Temperature-Mon | TEAMB07_ST_614_03_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_03_7.val | .1
16 | FC-614-06/07/08/09 pt100 input 8 | UA | - | HVAC | PT100-FC2 | 8 | Temperature | Mon | UA--:HVAC-PT100-FC2-8:Temperature-Mon | TEAMB08_ST_614_03_8.val | Inibido - BMS não lê | Analog | Input |  |  | C | TEAMB08_ST_614_03_8.val | .1
17 | FC-614-11/12/13/14 pt100 input 1 | UA | Hall-04C | HVAC | PT100-FC3 | 1 | Temperature | Mon | UA-Hall-04C:HVAC-PT100-FC3-1:Temperature-Mon | TEAMB01_ST_614_05_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_05_1.val | .1
18 | FC-614-11/12/13/14 pt100 input 2 | UA | Hall-05C | HVAC | PT100-FC3 | 2 | Temperature | Mon | UA-Hall-05C:HVAC-PT100-FC3-2:Temperature-Mon | TEAMB02_ST_614_05_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_05_2.val | .1
19 | FC-614-11/12/13/14 pt100 input 3 | UA | Hall-07C | HVAC | PT100-FC3 | 3 | Temperature | Mon | UA-Hall-07C:HVAC-PT100-FC3-3:Temperature-Mon | TEAMB03_ST_614_05_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_05_3.val | .1
20 | FC-614-11/12/13/14 pt100 input 4 | UA | Hall-08C | HVAC | PT100-FC3 | 4 | Temperature | Mon | UA-Hall-08C:HVAC-PT100-FC3-4:Temperature-Mon | TEAMB04_ST_614_05_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_05_4.val | .1
21 | FC-614-11/12/13/14 pt100 input 5 | UA | Halll-06B | HVAC | PT100-FC3 | 5 | Temperature | Mon | UA-Halll-06B:HVAC-PT100-FC3-5:Temperature-Mon | TEAMB05_ST_614_05_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_05_5.val | .1
22 | FC-614-11/12/13/14 pt100 input 6 | UA | Hall-08B | HVAC | PT100-FC3 | 6 | Temperature | Mon | UA-Hall-08B:HVAC-PT100-FC3-6:Temperature-Mon | TEAMB06_ST_614_05_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_05_6.val | .1
23 | FC-614-11/12/13/14 pt100 input 7 | UA | Hall-04D | HVAC | PT100-FC3 | 7 | Temperature | Mon | UA-Hall-04D:HVAC-PT100-FC3-7:Temperature-Mon | TEAMB07_ST_614_05_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_05_7.val | .1
24 | FC-614-11/12/13/14 pt100 input 8 | UA | Hall-07D | HVAC | PT100-FC3 | 8 | Temperature | Mon | UA-Hall-07D:HVAC-PT100-FC3-8:Temperature-Mon | TEAMB08_ST_614_05_8.val |  | Analog | Input |  |  | C | TEAMB08_ST_614_05_8.val | .1
25 | FC-614-16/17/18/19 pt100 input 1 | UA | Hall-10B | HVAC | PT100-FC4 | 1 | Temperature | Mon | UA-Hall-10B:HVAC-PT100-FC4-1:Temperature-Mon | TEAMB01_ST_614_07_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_07_1.val | .1
26 | FC-614-16/17/18/19 pt100 input 2 | UA | Hall-11B | HVAC | PT100-FC4 | 2 | Temperature | Mon | UA-Hall-11B:HVAC-PT100-FC4-2:Temperature-Mon | TEAMB02_ST_614_07_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_07_2.val | .1
27 | FC-614-16/17/18/19 pt100 input 3 | UA | Hall-13B | HVAC | PT100-FC4 | 3 | Temperature | Mon | UA-Hall-13B:HVAC-PT100-FC4-3:Temperature-Mon | TEAMB03_ST_614_07_3.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB03_ST_614_07_3.val | .1
28 | FC-614-16/17/18/19 pt100 input 4 | UA | Hall-13C | HVAC | PT100-FC4 | 4 | Temperature | Mon | UA-Hall-13C:HVAC-PT100-FC4-4:Temperature-Mon | TEAMB04_ST_614_07_4.val | Corrigir localização | Analog | Input |  |  | C | TEAMB04_ST_614_07_4.val | .1
29 | FC-614-16/17/18/19 pt100 input 5 | UA | Hall-15C | HVAC | PT100-FC4 | 5 | Temperature | Mon | UA-Hall-15C:HVAC-PT100-FC4-5:Temperature-Mon | TEAMB05_ST_614_07_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_07_5.val | .1
30 | FC-614-16/17/18/19 pt100 input 6 | UA | Hall-12C | HVAC | PT100-FC4 | 6 | Temperature | Mon | UA-Hall-12C:HVAC-PT100-FC4-6:Temperature-Mon | TEAMB06_ST_614_07_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_07_6.val | .1
31 | FC-614-16/17/18/19 pt100 input 7 | UA | Hall-10D | HVAC | PT100-FC4 | 7 | Temperature | Mon | UA-Hall-10D:HVAC-PT100-FC4-7:Temperature-Mon | TEAMB07_ST_614_07_7.val |  | Analog | Input |  |  | C | TEAMB07_ST_614_07_7.val | .1
32 | FC-614-16/17/18/19 pt100 input 8 | UA | Hall-13D | HVAC | PT100-FC4 | 8 | Temperature | Mon | UA-Hall-13D:HVAC-PT100-FC4-8:Temperature-Mon | TEAMB08_ST_614_07_8.val |  | Analog | Input |  |  | C | TEAMB08_ST_614_07_8.val | .1
33 | FC-614-21/22/23/24 pt100 input 1 | UA | Hall-15C | HVAC | PT100-FC5 | 1 | Temperature | Mon | UA-Hall-15C:HVAC-PT100-FC5-1:Temperature-Mon | TEAMB01_ST_614_09_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_09_1.val | .1
34 | FC-614-21/22/23/24 pt100 input 2 | UA | Hall-17C | HVAC | PT100-FC5 | 2 | Temperature | Mon | UA-Hall-17C:HVAC-PT100-FC5-2:Temperature-Mon | TEAMB02_ST_614_09_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_09_2.val | .1
35 | FC-614-21/22/23/24 pt100 input 3 | UA | Hall-19C | HVAC | PT100-FC5 | 3 | Temperature | Mon | UA-Hall-19C:HVAC-PT100-FC5-3:Temperature-Mon | TEAMB03_ST_614_09_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_09_3.val | .1
36 | FC-614-21/22/23/24 pt100 input 4 | UA | Hall-20C | HVAC | PT100-FC5 | 4 | Temperature | Mon | UA-Hall-20C:HVAC-PT100-FC5-4:Temperature-Mon | TEAMB04_ST_614_09_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_09_4.val | .1
37 | FC-614-21/22/23/24 pt100 input 5 | UA | Hall-17B | HVAC | PT100-FC5 | 5 | Temperature | Mon | UA-Hall-17B:HVAC-PT100-FC5-5:Temperature-Mon | TEAMB05_ST_614_09_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_09_5.val | .1
38 | FC-614-21/22/23/24 pt100 input 6 | UA | Hall-21B | HVAC | PT100-FC5 | 6 | Temperature | Mon | UA-Hall-21B:HVAC-PT100-FC5-6:Temperature-Mon | TEAMB06_ST_614_09_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_09_6.val | .1
39 | FC-614-21/22/23/24 pt100 input 7 | UA | Hall-19D | HVAC | PT100-FC5 | 7 | Temperature | Mon | UA-Hall-19D:HVAC-PT100-FC5-7:Temperature-Mon | TEAMB07_ST_614_09_7.val | Inibido - cartão em falha & Corrigir localização | Analog | Input |  |  | C | TEAMB07_ST_614_09_7.val | .1
40 | FC-614-21/22/23/24 pt100 input 8 | UA | Hall-16D | HVAC | PT100-FC5 | 8 | Temperature | Mon | UA-Hall-16D:HVAC-PT100-FC5-8:Temperature-Mon | TEAMB08_ST_614_09_8.val | Inibido - cartão em falha & Corrigir localização | Analog | Input |  |  | C | TEAMB08_ST_614_09_8.val | .1

## plc3
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | RS Logic | Nota | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec | PLC IP
41 | FC-614-26/27/28/29 pt100 input 1 | UA | Hall-22C | HVAC | PT100-FC6 | 1 | Temperature | Mon | UA-Hall-22C:HVAC-PT100-FC6-1:Temperature-Mon | TEAMB01_ST_614_11_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_11_1.val | .1
42 | FC-614-26/27/28/29 pt100 input 2 | UA | Hall-24C | HVAC | PT100-FC6 | 2 | Temperature | Mon | UA-Hall-24C:HVAC-PT100-FC6-2:Temperature-Mon | TEAMB02_ST_614_11_2.val |  | Analog | Input |  |  | C | TEAMB02_ST_614_11_2.val | .1
43 | FC-614-26/27/28/29 pt100 input 3 | UA | Hall-25C | HVAC | PT100-FC6 | 3 | Temperature | Mon | UA-Hall-25C:HVAC-PT100-FC6-3:Temperature-Mon | TEAMB03_ST_614_11_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_11_3.val | .1
44 | FC-614-26/27/28/29 pt100 input 4 | UA | Hall-26C | HVAC | PT100-FC6 | 4 | Temperature | Mon | UA-Hall-26C:HVAC-PT100-FC6-4:Temperature-Mon | TEAMB04_ST_614_11_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_11_4.val | .1
45 | FC-614-26/27/28/29 pt100 input 5 | UA | No-loca | HVAC | PT100-FC6 | 5 | Temperature | Mon | UA-No-loca:HVAC-PT100-FC6-5:Temperature-Mon | TEAMB05_ST_614_11_5.val | AS-BUILT (NO FC) BMS 25° | Analog | Input |  |  | C | TEAMB05_ST_614_11_5.val | .1
46 | FC-614-26/27/28/29 pt100 input 6 | UA | No-loca | HVAC | PT100-FC6 | 6 | Temperature | Mon | UA-No-loca:HVAC-PT100-FC6-6:Temperature-Mon | TEAMB06_ST_614_11_6.val | AS-BUILT (NO FC) BMS 25° | Analog | Input |  |  | C | TEAMB06_ST_614_11_6.val | .1
47 | FC-614-26/27/28/29 pt100 input 7 | UA | Hall-22D | HVAC | PT100-FC6 | 7 | Temperature | Mon | UA-Hall-22D:HVAC-PT100-FC6-7:Temperature-Mon | TEAMB07_ST_614_11_7.val | AS-BUILT (NO FC) BMS 25° | Analog | Input |  |  | C | TEAMB07_ST_614_11_7.val | .1
48 | FC-614-26/27/28/29 pt100 input 8 | UA | Hall-25D | HVAC | PT100-FC6 | 8 | Temperature | Mon | UA-Hall-25D:HVAC-PT100-FC6-8:Temperature-Mon | TEAMB08_ST_614_11_8.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB08_ST_614_11_8.val | .1
49 | FC-614-32/33/34/35 pt100 input 1 | UA | Hall-32C | HVAC | PT100-FC7 | 1 | Temperature | Mon | UA-Hall-32C:HVAC-PT100-FC7-1:Temperature-Mon | TEAMB01_ST_614_13_1.val |  | Analog | Input |  |  | C | TEAMB01_ST_614_13_1.val | .1
50 | FC-614-32/33/34/35 pt100 input 2 | UA | Hall-31C | HVAC | PT100-FC7 | 2 | Temperature | Mon | UA-Hall-31C:HVAC-PT100-FC7-2:Temperature-Mon | TEAMB02_ST_614_13_2.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB02_ST_614_13_2.val | .1
51 | FC-614-32/33/34/35 pt100 input 3 | UA | Hall-29C | HVAC | PT100-FC7 | 3 | Temperature | Mon | UA-Hall-29C:HVAC-PT100-FC7-3:Temperature-Mon | TEAMB03_ST_614_13_3.val |  | Analog | Input |  |  | C | TEAMB03_ST_614_13_3.val | .1
52 | FC-614-32/33/34/35 pt100 input 4 | UA | Hall-28C | HVAC | PT100-FC7 | 4 | Temperature | Mon | UA-Hall-28C:HVAC-PT100-FC7-4:Temperature-Mon | TEAMB04_ST_614_13_4.val |  | Analog | Input |  |  | C | TEAMB04_ST_614_13_4.val | .1
53 | FC-614-32/33/34/35 pt100 input 5 | UA | Hall-29B | HVAC | PT100-FC7 | 5 | Temperature | Mon | UA-Hall-29B:HVAC-PT100-FC7-5:Temperature-Mon | TEAMB05_ST_614_13_5.val | Corrigir localização | Analog | Input |  |  | C | TEAMB05_ST_614_13_5.val | .1
54 | FC-614-32/33/34/35 pt100 input 6 | UA | Hall-32B | HVAC | PT100-FC7 | 6 | Temperature | Mon | UA-Hall-32B:HVAC-PT100-FC7-6:Temperature-Mon | TEAMB06_ST_614_13_6.val | Corrigir localização | Analog | Input |  |  | C | TEAMB06_ST_614_13_6.val | .1
55 | FC-614-32/33/34/35 pt100 input 7 | UA | Hall-28D | HVAC | PT100-FC7 | 7 | Temperature | Mon | UA-Hall-28D:HVAC-PT100-FC7-7:Temperature-Mon | TEAMB07_ST_614_13_7.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB07_ST_614_13_7.val | .1
56 | FC-614-32/33/34/35 pt100 input 8 | UA | Hall-31D | HVAC | PT100-FC7 | 8 | Temperature | Mon | UA-Hall-31D:HVAC-PT100-FC7-8:Temperature-Mon | TEAMB08_ST_614_13_8.val | Inibido - mau contato | Analog | Input |  |  | C | TEAMB08_ST_614_13_8.val | .1