## Petra 7 Skid
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Nota | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec | PV antiga
1 | Temperature Indicating Cooler Valve 01 Opening Percentage Ref | UA | B19C20SkidP7 | HD | TCV | 421 | MVValue | Mon | UA-B19C20SkidP7:HD-TCV-421:MVValue-Mon | UA-B19C20SkidP7:HD-TCV-421:MVValueUpperLimit-Cte | UA-B19C20SkidP7:HD-TCV-421:MVValueLowerLimit-Cte | TCV421.Reference_Value | Adicionar se for necessário registrar qual a válvula que está trabalhando, TIC421.SO já registra a saída, mas não para qual válvula | Analog | Input | 100 | 0 | % | TCV421.Reference_Value | 1 | 2 | UA:B19C20SkidP7:HD-TCV-01:ValveOpening-Mon
2 | Temperature Indicating Cooler Valve 02 Opening Percentage Ref | UA | B19C20SkidP7 | HD | TCV | 422 | MVValue | Mon | UA-B19C20SkidP7:HD-TCV-422:MVValue-Mon | UA-B19C20SkidP7:HD-TCV-422:MVValueUpperLimit-Cte | UA-B19C20SkidP7:HD-TCV-422:MVValueLowerLimit-Cte | TCV422.Reference_Value | Adicionar se for necessário registrar qual a válvula que está trabalhando, TIC421.SO já registra a saída, mas não para qual válvula | Analog | Input | 100 | 0 | % | TCV422.Reference_Value | 1 | 2 | UA:B19C20SkidP7:HD-TCV-02:ValveOpening-Mon
3 | Temperature Indicating Cooler pv Mon | UA | B19C20SkidP7 | HD | TIC | TCV | Tempeture | Mon | UA-B19C20SkidP7:HD-TIC-TCV:Tempeture-Mon | UA-B19C20SkidP7:HD-TIC-TCV:TempetureUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-TCV:TempetureLowerLimit-Cte | TIC421.PV | Leitura | Analog | Input | 150 | 0 | C | TIC421.PV | 1 | 2 | UA:B19C20SkidP7:HD-TIC-01:Temperature-Mon
4 | Temperature Indicating Cooler kd Sp | UA | B19C20SkidP7 | HD | TIC | TCV | LoopPIDKd | SP | UA-B19C20SkidP7:HD-TIC-TCV:LoopPIDKd-SP | UA-B19C20SkidP7:HD-TIC-TCV:LoopPIDKdUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-TCV:LoopPIDKdLowerLimit-Cte | TIC421.KD | leitura/escrita | Analog | Output | 2147483647 | 0 |  | TIC421.KD | 1 | 5 | UA:B19C20SkidP7:HD-TIC-01:Kd-RB
5 | Temperature Indicating Cooler ki Sp | UA | B19C20SkidP7 | HD | TIC | TCV | LoopPIDKi | SP | UA-B19C20SkidP7:HD-TIC-TCV:LoopPIDKi-SP | UA-B19C20SkidP7:HD-TIC-TCV:LoopPIDKiUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-TCV:LoopPIDKiLowerLimit-Cte | TIC421.KI | leitura/escrita | Analog | Output | 2147483647 | 0 |  | TIC421.KI | 1 | 5 | UA:B19C20SkidP7:HD-TIC-01:Ki-RB
6 | Temperature Indicating Cooler kp Sp | UA | B19C20SkidP7 | HD | TIC | TCV | LoopPIDKp | SP | UA-B19C20SkidP7:HD-TIC-TCV:LoopPIDKp-SP | UA-B19C20SkidP7:HD-TIC-TCV:LoopPIDKpUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-TCV:LoopPIDKpLowerLimit-Cte | TIC421.KP | leitura/escrita | Analog | Output | 2147483647 | 0 |  | TIC421.KP | 1 | 5 | UA:B19C20SkidP7:HD-TIC-01:Kp-RB
7 | Temperature Indicating Cooler Valves Opening Percentage Ref | UA | B19C20SkidP7 | HD | TIC | TCV | MVManualRef | SP | UA-B19C20SkidP7:HD-TIC-TCV:MVManualRef-SP | UA-B19C20SkidP7:HD-TIC-TCV:MVManualRefUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-TCV:MVManualRefLowerLimit-Cte | TIC421.SO | leitura/escrita - só aceita escrita em manual | Analog | Output | 100 | 0 | % | TIC421.SO | 1 | 2 | #N/A
8 | Temperature Indicating Cooler and Heater Temperature Ref | UA | B19C20SkidP7 | HD | TIC |  | TemperatureRef | SP | UA-B19C20SkidP7:HD-TIC-:TemperatureRef-SP | UA-B19C20SkidP7:HD-TIC-:TemperatureRefUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-:TemperatureRefLowerLimit-Cte | TIC422_SP_Local | leitura/escrita | Analog | Output | 100 | 0 | C | TIC422_SP_Local | 1 | 2 | #N/A
9 | Temperature Indicating Heater Resistance 01 Power Percentage Mon | UA | B19C20SkidP7 | HD | RE | 421 | MVValue | Mon | UA-B19C20SkidP7:HD-RE-421:MVValue-Mon | UA-B19C20SkidP7:HD-RE-421:MVValueUpperLimit-Cte | UA-B19C20SkidP7:HD-RE-421:MVValueLowerLimit-Cte | RE421_Ref.Reference_Value | leitura - o que está sendo enviado para campo (tanto manual como auto) | Analog | Input | 100 | 0 | % | RE421_Ref.Reference_Value | 1 | 2 | UA:B19C20SkidP7:HD-RE-01:TemperatureRef-Mon
10 | Temperature Indicating Heater Resistance 02 Power Percentage Mon | UA | B19C20SkidP7 | HD | RE | 422 | MVValue | Mon | UA-B19C20SkidP7:HD-RE-422:MVValue-Mon | UA-B19C20SkidP7:HD-RE-422:MVValueUpperLimit-Cte | UA-B19C20SkidP7:HD-RE-422:MVValueLowerLimit-Cte | RE422_Ref.Reference_Value | leitura - o que está sendo enviado para campo (tanto manual como auto) | Analog | Input | 100 | 0 | % | RE422_Ref.Reference_Value | 1 | 2 | UA:B19C20SkidP7:HD-RE-02:TemperatureRef-Mon
11 | Temperature Indicating Heater pv Mon | UA | B19C20SkidP7 | HD | TIC | RE | Temperature | Mon | UA-B19C20SkidP7:HD-TIC-RE:Temperature-Mon | UA-B19C20SkidP7:HD-TIC-RE:TemperatureUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-RE:TemperatureLowerLimit-Cte | TIC422.PV | Leitura | Analog | Input | 150 | 0 | C | TIC422.PV | 1 | 2 | UA:B19C20SkidP7:HD-TIC-02:Temperature-Mon
12 | Temperature Indicating Heater Resistance 01 Power Percentage Manual Ref | UA | B19C20SkidP7 | HD | RE | 421 | MVManualRef | SP | UA-B19C20SkidP7:HD-RE-421:MVManualRef-SP | UA-B19C20SkidP7:HD-RE-421:MVManualRefUpperLimit-Cte | UA-B19C20SkidP7:HD-RE-421:MVManualRefLowerLimit-Cte | RE421.Ref_Man | leitura/escrita - altera a qq momento, mas saída só respeita quando em manual | Analog | Output | 100 | 0 | % | RE421.Ref_Man | 1 | 2 | #N/A
13 | Temperature Indicating Heater Resistance 02 Power Percentage Manual Ref | UA | B19C20SkidP7 | HD | RE | 422 | MVManualRef | SP | UA-B19C20SkidP7:HD-RE-422:MVManualRef-SP | UA-B19C20SkidP7:HD-RE-422:MVManualRefUpperLimit-Cte | UA-B19C20SkidP7:HD-RE-422:MVManualRefLowerLimit-Cte | RE422.Ref_Man | leitura/escrita - altera a qq momento, mas saída só respeita quando em manual | Analog | Output | 100 | 0 | % | RE422.Ref_Man | 1 | 2 | #N/A
14 | Temperature Indicating Heater kd Sp | UA | B19C20SkidP7 | HD | TIC | RE | LoopPIDKd | SP | UA-B19C20SkidP7:HD-TIC-RE:LoopPIDKd-SP | UA-B19C20SkidP7:HD-TIC-RE:LoopPIDKdUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-RE:LoopPIDKdLowerLimit-Cte | TIC422.KD | leitura/escrita | Analog | Output | 2147483647 | 0 |  | TIC422.KD | 1 | 5 | UA:B19C20SkidP7:HD-TIC-02:Kd-RB
15 | Temperature Indicating Heater ki Sp | UA | B19C20SkidP7 | HD | TIC | RE | LoopPIDKi | SP | UA-B19C20SkidP7:HD-TIC-RE:LoopPIDKi-SP | UA-B19C20SkidP7:HD-TIC-RE:LoopPIDKiUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-RE:LoopPIDKiLowerLimit-Cte | TIC422.KI | leitura/escrita | Analog | Output | 2147483647 | 0 |  | TIC422.KI | 1 | 5 | UA:B19C20SkidP7:HD-TIC-02:Ki-RB
16 | Temperature Indicating Heater kp Sp | UA | B19C20SkidP7 | HD | TIC | RE | LoopPIDKp | SP | UA-B19C20SkidP7:HD-TIC-RE:LoopPIDKp-SP | UA-B19C20SkidP7:HD-TIC-RE:LoopPIDKpUpperLimit-Cte | UA-B19C20SkidP7:HD-TIC-RE:LoopPIDKpLowerLimit-Cte | TIC422.KP | leitura/escrita | Analog | Output | 2147483647 | 0 |  | TIC422.KP | 1 | 5 | UA:B19C20SkidP7:HD-TIC-02:Kp-RB
17 | Power Indicating Pump 01 Power Percentage Mon | UA | B19C20SkidP7 | HD | BC | 421 | MVValue | Mon | UA-B19C20SkidP7:HD-BC-421:MVValue-Mon | UA-B19C20SkidP7:HD-BC-421:MVValueUpperLimit-Cte | UA-B19C20SkidP7:HD-BC-421:MVValueLowerLimit-Cte | BC421Ref.Reference_Value | leitura - o que está sendo enviado para campo (tanto manual como auto) | Analog | Input | 100 | 0 | % | BC421Ref.Reference_Value | 1 | 2 | #N/A
18 | Power Indicating Pump 02 Power Percentage Mon | UA | B19C20SkidP7 | HD | BC | 422 | MVValue | Mon | UA-B19C20SkidP7:HD-BC-422:MVValue-Mon | UA-B19C20SkidP7:HD-BC-422:MVValueUpperLimit-Cte | UA-B19C20SkidP7:HD-BC-422:MVValueLowerLimit-Cte | BC422Ref.Reference_Value | leitura - o que está sendo enviado para campo (tanto manual como auto) | Analog | Input | 100 | 0 | % | BC422Ref.Reference_Value | 1 | 2 | #N/A
19 | Pressure Indicating Pump pv Mon | UA | B19C20SkidP7 | HD | PIC | BC | Pressure | Mon | UA-B19C20SkidP7:HD-PIC-BC:Pressure-Mon | UA-B19C20SkidP7:HD-PIC-BC:PressureUpperLimit-Cte | UA-B19C20SkidP7:HD-PIC-BC:PressureLowerLimit-Cte | PIC421.PV | igual ao PT421.Scaled_Value | Analog | Input | 10 | 0 | bar | PIC421.PV | 1 | 2 | UA:B19C20SkidP7:HD-BC-01:Pressure-Mon
20 | Pressure Indicating Pump ki Rb | UA | B19C20SkidP7 | HD | PIC | BC | LoopPIDKd | RB | UA-B19C20SkidP7:HD-PIC-BC:LoopPIDKd-RB | UA-B19C20SkidP7:HD-PIC-BC:LoopPIDKdUpperLimit-Cte | UA-B19C20SkidP7:HD-PIC-BC:LoopPIDKdLowerLimit-Cte | PIC421.KD | leitura/escrita | Analog | Input | 2147483647 | 0 |  | PIC421.KD | 1 | 5 | UA:B19C20SkidP7:HD-PIC-01:Kd-RB
21 | Pressure Indicating Pump kd Rb | UA | B19C20SkidP7 | HD | PIC | BC | LoopPIDKi | RB | UA-B19C20SkidP7:HD-PIC-BC:LoopPIDKi-RB | UA-B19C20SkidP7:HD-PIC-BC:LoopPIDKiUpperLimit-Cte | UA-B19C20SkidP7:HD-PIC-BC:LoopPIDKiLowerLimit-Cte | PIC421.KI | leitura/escrita | Analog | Input | 2147483647 | 0 |  | PIC421.KI | 1 | 5 | UA:B19C20SkidP7:HD-PIC-01:Ki-RB
22 | Pressure Indicating Pump kp Rb | UA | B19C20SkidP7 | HD | PIC | BC | LoopPIDKp | RB | UA-B19C20SkidP7:HD-PIC-BC:LoopPIDKp-RB | UA-B19C20SkidP7:HD-PIC-BC:LoopPIDKpUpperLimit-Cte | UA-B19C20SkidP7:HD-PIC-BC:LoopPIDKpLowerLimit-Cte | PIC421.KP | leitura/escrita | Analog | Input | 2147483647 | 0 |  | PIC421.KP | 1 | 5 | UA:B19C20SkidP7:HD-PIC-01:Kp-RB
23 | Pressure Indicating Pump Pressure Ref | UA | B19C20SkidP7 | HD | PIC | BC | PressureRef | RB | UA-B19C20SkidP7:HD-PIC-BC:PressureRef-RB | UA-B19C20SkidP7:HD-PIC-BC:PressureRefUpperLimit-Cte | UA-B19C20SkidP7:HD-PIC-BC:PressureRefLowerLimit-Cte | PIC422_SP_Local | leitura/escrita | Analog | Input | 10 | 0 | bar | PIC422_SP_Local | 1 | 2 | #N/A
24 | Water Flow Transmitter 421 | UA | B19C20SkidP7 | HD | FT | 421 | Flow | Mon | UA-B19C20SkidP7:HD-FT-421:Flow-Mon | UA-B19C20SkidP7:HD-FT-421:FlowUpperLimit-Cte | UA-B19C20SkidP7:HD-FT-421:FlowLowerLimit-Cte | FT421.Scaled_Value | Leitura | Analog | Input | 20 | 0 | m3/h | FT421.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-FT-01:Flow-Mon
25 | Water Flow Transmitter 422 | UA | B19C20SkidP7 | HD | FT | 422 | Flow | Mon | UA-B19C20SkidP7:HD-FT-422:Flow-Mon | UA-B19C20SkidP7:HD-FT-422:FlowUpperLimit-Cte | UA-B19C20SkidP7:HD-FT-422:FlowLowerLimit-Cte | FT422.Scaled_Value | Leitura | Analog | Input | 20 | 0 | m3/h | FT422.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-FT-02:Flow-Mon
26 | Water Flow Transmitter 423 | UA | B19C20SkidP7 | HD | FT | 423 | Flow | Mon | UA-B19C20SkidP7:HD-FT-423:Flow-Mon | UA-B19C20SkidP7:HD-FT-423:FlowUpperLimit-Cte | UA-B19C20SkidP7:HD-FT-423:FlowLowerLimit-Cte | FT423.Scaled_Value | Leitura | Analog | Input | 20 | 0 | m3/h | FT423.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-FT-03:Flow-Mon
27 | Water Pressure Transmitter 421 | UA | B19C20SkidP7 | HD | PT | 421 | Pressure | Mon | UA-B19C20SkidP7:HD-PT-421:Pressure-Mon | UA-B19C20SkidP7:HD-PT-421:PressureUpperLimit-Cte | UA-B19C20SkidP7:HD-PT-421:PressureLowerLimit-Cte | PT421.Scaled_Value | Leitura | Analog | Input | 10 | 0 | bar | PT421.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-PT-01:Pressure-Mon
28 | Water Pressure Transmitter 422 | UA | B19C20SkidP7 | HD | PT | 422 | Pressure | Mon | UA-B19C20SkidP7:HD-PT-422:Pressure-Mon | UA-B19C20SkidP7:HD-PT-422:PressureUpperLimit-Cte | UA-B19C20SkidP7:HD-PT-422:PressureLowerLimit-Cte | PT422.Scaled_Value | Leitura | Analog | Input | 10 | 0 | bar | PT422.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-PT-02:Pressure-Mon
29 | Water Pressure Transmitter 423 | UA | B19C20SkidP7 | HD | PT | 423 | Pressure | Mon | UA-B19C20SkidP7:HD-PT-423:Pressure-Mon | UA-B19C20SkidP7:HD-PT-423:PressureUpperLimit-Cte | UA-B19C20SkidP7:HD-PT-423:PressureLowerLimit-Cte | PT423.Scaled_Value | Leitura | Analog | Input | 10 | 0 | bar | PT423.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-PT-03:Pressure-Mon
30 | Water Pressure Transmitter 424 | UA | B19C20SkidP7 | HD | PT | 424 | Pressure | Mon | UA-B19C20SkidP7:HD-PT-424:Pressure-Mon | UA-B19C20SkidP7:HD-PT-424:PressureUpperLimit-Cte | UA-B19C20SkidP7:HD-PT-424:PressureLowerLimit-Cte | PT424.Scaled_Value | Leitura | Analog | Input | 10 | 0 | bar | PT424.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-PT-04:Pressure-Mon
31 | Water Temperature Transmitter EXT | UA | B19C20SkidP7 | HD | TT | EXT | Temperature | Mon | UA-B19C20SkidP7:HD-TT-EXT:Temperature-Mon | UA-B19C20SkidP7:HD-TT-EXT:TemperatureUpperLimit-Cte | UA-B19C20SkidP7:HD-TT-EXT:TemperatureLowerLimit-Cte | TT_EXT.Scaled_Value | Leitura | Analog | Input | 150 | 0 | C | TT_EXT.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-TT-EXT:Temperature-Mon
32 | Water Temperature Transmitter 421 | UA | B19C20SkidP7 | HD | TT | 421 | Temperature | Mon | UA-B19C20SkidP7:HD-TT-421:Temperature-Mon | UA-B19C20SkidP7:HD-TT-421:TemperatureUpperLimit-Cte | UA-B19C20SkidP7:HD-TT-421:TemperatureLowerLimit-Cte | TT421.Scaled_Value | Leitura | Analog | Input | 150 | 0 | C | TT421.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-TT-01:Temperature-Mon
33 | Water Temperature Transmitter 422 | UA | B19C20SkidP7 | HD | TT | 422 | Temperature | Mon | UA-B19C20SkidP7:HD-TT-422:Temperature-Mon | UA-B19C20SkidP7:HD-TT-422:TemperatureUpperLimit-Cte | UA-B19C20SkidP7:HD-TT-422:TemperatureLowerLimit-Cte | TT422.Scaled_Value | Leitura | Analog | Input | 150 | 0 | C | TT422.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-TT-02:Temperature-Mon
34 | Water Temperature Transmitter 423 | UA | B19C20SkidP7 | HD | TT | 423 | Temperature | Mon | UA-B19C20SkidP7:HD-TT-423:Temperature-Mon | UA-B19C20SkidP7:HD-TT-423:TemperatureUpperLimit-Cte | UA-B19C20SkidP7:HD-TT-423:TemperatureLowerLimit-Cte | TT423.Scaled_Value | Leitura | Analog | Input | 150 | 0 | C | TT423.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-TT-03:Temperature-Mon
35 | Water Temperature Transmitter 424 | UA | B19C20SkidP7 | HD | TT | 424 | Temperature | Mon | UA-B19C20SkidP7:HD-TT-424:Temperature-Mon | UA-B19C20SkidP7:HD-TT-424:TemperatureUpperLimit-Cte | UA-B19C20SkidP7:HD-TT-424:TemperatureLowerLimit-Cte | TT424.Scaled_Value | Leitura | Analog | Input | 150 | 0 | C | TT424.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-TT-04:Temperature-Mon
36 | Water Temperature Transmitter 425 | UA | B19C20SkidP7 | HD | TT | 425 | Temperature | Mon | UA-B19C20SkidP7:HD-TT-425:Temperature-Mon | UA-B19C20SkidP7:HD-TT-425:TemperatureUpperLimit-Cte | UA-B19C20SkidP7:HD-TT-425:TemperatureLowerLimit-Cte | TT425.Scaled_Value | Leitura | Analog | Input | 150 | 0 | C | TT425.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-TT-05:Temperature-Mon
37 | Water Temperature Transmitter 426 | UA | B19C20SkidP7 | HD | TT | 426 | Temperature | Mon | UA-B19C20SkidP7:HD-TT-426:Temperature-Mon | UA-B19C20SkidP7:HD-TT-426:TemperatureUpperLimit-Cte | UA-B19C20SkidP7:HD-TT-426:TemperatureLowerLimit-Cte | TT426.Scaled_Value | Leitura | Analog | Input | 150 | 0 | C | TT426.Scaled_Value | 1 | 2 | UA:B19C20SkidP7:HD-TT-06:Temperature-Mon
Note on Q5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2^31-1?
Note on Q6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2^31-1?
Note on Q7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2^31-1?
Note on Q15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2^31-1?
Note on Q16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2^31-1?
Note on Q17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2^31-1?
Note on Q21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2^31-1?
Note on Q22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2^31-1?
Note on Q23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2^31-1?

## SSAmp Tower 04 CLP
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec | Cmd Duration | PV Conversion | Upper Limit Conversion | Lower Limit Conversion
1 | AC da Torre 04 do Anel Status | RA | ToSIA04 | RF | ACPanel | - | PwrACOp | Mon | RA-ToSIA04:RF-ACPanel:PwrACOp-Mon |  |  | RA_ToSIA04_RF_ACPanel_PwrACOpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_ACPanel_PwrACOpMon | .1
2 | AC das Fontes TDK Torre 04 Off | RA | ToSIA04 | RF | ACPanel | - | PwrACDsbl | Sel | RA-ToSIA04:RF-ACPanel:PwrACDsbl-Sel |  |  | RA_ToSIA04_RF_ACPanel_PwrACDsblSel | Digital | Control |  |  |  | RA_ToSIA04_RF_ACPanel_PwrACDsblSel | .1 |  | 0.5
3 | AC das Fontes TDK Torre 04 On | RA | ToSIA04 | RF | ACPanel | - | PwrACEnbl | Sel | RA-ToSIA04:RF-ACPanel:PwrACEnbl-Sel |  |  | RA_ToSIA04_RF_ACPanel_PwrACEnblSel | Digital | Control |  |  |  | RA_ToSIA04_RF_ACPanel_PwrACEnblSel | .1 |  | 0.5
4 | AC das Fontes TDK Torre 04 Status | RA | ToSIA04 | RF | ACPanel | - | PwrAC | Sts | RA-ToSIA04:RF-ACPanel:PwrAC-Sts |  |  | RA_ToSIA04_RF_ACPanel_PwrACSts | Digital | Output |  |  |  | RA_ToSIA04_RF_ACPanel_PwrACSts | .1
5 | Falta de Fase do Painel Torre 04 do Anel | RA | ToSIA04 | RF | ACPanel | - | PhsFlt | Mon | RA-ToSIA04:RF-ACPanel:PhsFlt-Mon |  |  | RA_ToSIA04_RF_ACPanel_PhsFltMon | Digital | Input |  |  |  | RA_ToSIA04_RF_ACPanel_PhsFltMon | .1
6 | Interlock externo do Painel Torre 04 | RA | ToSIA04 | RF | ACPanel | - | Intlk | Mon | RA-ToSIA04:RF-ACPanel:Intlk-Mon |  |  | RA_ToSIA04_RF_ACPanel_IntlkMon | Digital | Input |  |  |  | RA_ToSIA04_RF_ACPanel_IntlkMon | .1
7 | PT-100 da Barra Dissipadora 01A | RA | ToSIA04 | RF | HeatSink | H01A | T | Mon | RA-ToSIA04:RF-HeatSink-H01A:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H01A_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H01A_TMon | .5 | 2 |  | pv | pv | pv
8 | PT-100 da Barra Dissipadora 01B | RA | ToSIA04 | RF | HeatSink | H01B | T | Mon | RA-ToSIA04:RF-HeatSink-H01B:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H01B_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H01B_TMon | .5 | 2 |  | pv | pv | pv
9 | PT-100 da Barra Dissipadora 02A | RA | ToSIA04 | RF | HeatSink | H02A | T | Mon | RA-ToSIA04:RF-HeatSink-H02A:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H02A_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H02A_TMon | .5 | 2 |  | pv | pv | pv
10 | PT-100 da Barra Dissipadora 02B | RA | ToSIA04 | RF | HeatSink | H02B | T | Mon | RA-ToSIA04:RF-HeatSink-H02B:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H02B_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H02B_TMon | .5 | 2 |  | pv | pv | pv
11 | PT-100 da Barra Dissipadora 03A | RA | ToSIA04 | RF | HeatSink | H03A | T | Mon | RA-ToSIA04:RF-HeatSink-H03A:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H03A_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H03A_TMon | .5 | 2 |  | pv | pv | pv
12 | PT-100 da Barra Dissipadora 03B | RA | ToSIA04 | RF | HeatSink | H03B | T | Mon | RA-ToSIA04:RF-HeatSink-H03B:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H03B_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H03B_TMon | .5 | 2 |  | pv | pv | pv
13 | PT-100 da Barra Dissipadora 04A | RA | ToSIA04 | RF | HeatSink | H04A | T | Mon | RA-ToSIA04:RF-HeatSink-H04A:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H04A_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H04A_TMon | .5 | 2 |  | pv | pv | pv
14 | PT-100 da Barra Dissipadora 04B | RA | ToSIA04 | RF | HeatSink | H04B | T | Mon | RA-ToSIA04:RF-HeatSink-H04B:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H04B_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H04B_TMon | .5 | 2 |  | pv | pv | pv
15 | PT-100 da Barra Dissipadora 05A | RA | ToSIA04 | RF | HeatSink | H05A | T | Mon | RA-ToSIA04:RF-HeatSink-H05A:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H05A_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H05A_TMon | .5 | 2 |  | pv | pv | pv
16 | PT-100 da Barra Dissipadora 05B | RA | ToSIA04 | RF | HeatSink | H05B | T | Mon | RA-ToSIA04:RF-HeatSink-H05B:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H05B_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H05B_TMon | .5 | 2 |  | pv | pv | pv
17 | PT-100 da Barra Dissipadora 06A | RA | ToSIA04 | RF | HeatSink | H06A | T | Mon | RA-ToSIA04:RF-HeatSink-H06A:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H06A_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H06A_TMon | .5 | 2 |  | pv | pv | pv
18 | PT-100 da Barra Dissipadora 06B | RA | ToSIA04 | RF | HeatSink | H06B | T | Mon | RA-ToSIA04:RF-HeatSink-H06B:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H06B_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H06B_TMon | .5 | 2 |  | pv | pv | pv
19 | PT-100 da Barra Dissipadora 07A | RA | ToSIA04 | RF | HeatSink | H07A | T | Mon | RA-ToSIA04:RF-HeatSink-H07A:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H07A_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H07A_TMon | .5 | 2 |  | pv | pv | pv
20 | PT-100 da Barra Dissipadora 07B | RA | ToSIA04 | RF | HeatSink | H07B | T | Mon | RA-ToSIA04:RF-HeatSink-H07B:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H07B_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H07B_TMon | .5 | 2 |  | pv | pv | pv
21 | PT-100 da Barra Dissipadora 08A | RA | ToSIA04 | RF | HeatSink | H08A | T | Mon | RA-ToSIA04:RF-HeatSink-H08A:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H08A_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H08A_TMon | .5 | 2 |  | pv | pv | pv
22 | PT-100 da Barra Dissipadora 08B | RA | ToSIA04 | RF | HeatSink | H08B | T | Mon | RA-ToSIA04:RF-HeatSink-H08B:T-Mon |  |  | RA_ToSIA04_RF_HeatSink_H08B_TMon | Analog | Input |  |  | C | RA_ToSIA04_RF_HeatSink_H08B_TMon | .5 | 2 |  | pv | pv | pv
23 | Temperatura abaixo do set da Barra Dissipadora 01A | RA | ToSIA04 | RF | HeatSink | H01A | TDown | Mon | RA-ToSIA04:RF-HeatSink-H01A:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H01A_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H01A_TDownMon | .1
24 | Temperatura abaixo do set da Barra Dissipadora 01B | RA | ToSIA04 | RF | HeatSink | H01B | TDown | Mon | RA-ToSIA04:RF-HeatSink-H01B:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H01B_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H01B_TDownMon | .1
25 | Temperatura abaixo do set da Barra Dissipadora 02A | RA | ToSIA04 | RF | HeatSink | H02A | TDown | Mon | RA-ToSIA04:RF-HeatSink-H02A:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H02A_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H02A_TDownMon | .1
26 | Temperatura abaixo do set da Barra Dissipadora 02B | RA | ToSIA04 | RF | HeatSink | H02B | TDown | Mon | RA-ToSIA04:RF-HeatSink-H02B:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H02B_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H02B_TDownMon | .1
27 | Temperatura abaixo do set da Barra Dissipadora 03A | RA | ToSIA04 | RF | HeatSink | H03A | TDown | Mon | RA-ToSIA04:RF-HeatSink-H03A:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H03A_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H03A_TDownMon | .1
28 | Temperatura abaixo do set da Barra Dissipadora 03B | RA | ToSIA04 | RF | HeatSink | H03B | TDown | Mon | RA-ToSIA04:RF-HeatSink-H03B:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H03B_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H03B_TDownMon | .1
29 | Temperatura abaixo do set da Barra Dissipadora 04A | RA | ToSIA04 | RF | HeatSink | H04A | TDown | Mon | RA-ToSIA04:RF-HeatSink-H04A:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H04A_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H04A_TDownMon | .1
30 | Temperatura abaixo do set da Barra Dissipadora 04B | RA | ToSIA04 | RF | HeatSink | H04B | TDown | Mon | RA-ToSIA04:RF-HeatSink-H04B:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H04B_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H04B_TDownMon | .1
31 | Temperatura abaixo do set da Barra Dissipadora 05A | RA | ToSIA04 | RF | HeatSink | H05A | TDown | Mon | RA-ToSIA04:RF-HeatSink-H05A:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H05A_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H05A_TDownMon | .1
32 | Temperatura abaixo do set da Barra Dissipadora 05B | RA | ToSIA04 | RF | HeatSink | H05B | TDown | Mon | RA-ToSIA04:RF-HeatSink-H05B:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H05B_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H05B_TDownMon | .1
33 | Temperatura abaixo do set da Barra Dissipadora 06A | RA | ToSIA04 | RF | HeatSink | H06A | TDown | Mon | RA-ToSIA04:RF-HeatSink-H06A:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H06A_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H06A_TDownMon | .1
34 | Temperatura abaixo do set da Barra Dissipadora 06B | RA | ToSIA04 | RF | HeatSink | H06B | TDown | Mon | RA-ToSIA04:RF-HeatSink-H06B:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H06B_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H06B_TDownMon | .1
35 | Temperatura abaixo do set da Barra Dissipadora 07A | RA | ToSIA04 | RF | HeatSink | H07A | TDown | Mon | RA-ToSIA04:RF-HeatSink-H07A:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H07A_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H07A_TDownMon | .1
36 | Temperatura abaixo do set da Barra Dissipadora 07B | RA | ToSIA04 | RF | HeatSink | H07B | TDown | Mon | RA-ToSIA04:RF-HeatSink-H07B:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H07B_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H07B_TDownMon | .1
37 | Temperatura abaixo do set da Barra Dissipadora 08A | RA | ToSIA04 | RF | HeatSink | H08A | TDown | Mon | RA-ToSIA04:RF-HeatSink-H08A:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H08A_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H08A_TDownMon | .1
38 | Temperatura abaixo do set da Barra Dissipadora 08B | RA | ToSIA04 | RF | HeatSink | H08B | TDown | Mon | RA-ToSIA04:RF-HeatSink-H08B:TDown-Mon |  |  | RA_ToSIA04_RF_HeatSink_H08B_TDownMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H08B_TDownMon | .1
39 | Temperatura acima do set da Barra Dissipadora 01A | RA | ToSIA04 | RF | HeatSink | H01A | TUp | Mon | RA-ToSIA04:RF-HeatSink-H01A:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H01A_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H01A_TUpMon | .1
40 | Temperatura acima do set da Barra Dissipadora 01B | RA | ToSIA04 | RF | HeatSink | H01B | TUp | Mon | RA-ToSIA04:RF-HeatSink-H01B:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H01B_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H01B_TUpMon | .1
41 | Temperatura acima do set da Barra Dissipadora 02A | RA | ToSIA04 | RF | HeatSink | H02A | TUp | Mon | RA-ToSIA04:RF-HeatSink-H02A:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H02A_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H02A_TUpMon | .1
42 | Temperatura acima do set da Barra Dissipadora 02B | RA | ToSIA04 | RF | HeatSink | H02B | TUp | Mon | RA-ToSIA04:RF-HeatSink-H02B:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H02B_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H02B_TUpMon | .1
43 | Temperatura acima do set da Barra Dissipadora 03A | RA | ToSIA04 | RF | HeatSink | H03A | TUp | Mon | RA-ToSIA04:RF-HeatSink-H03A:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H03A_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H03A_TUpMon | .1
44 | Temperatura acima do set da Barra Dissipadora 03B | RA | ToSIA04 | RF | HeatSink | H03B | TUp | Mon | RA-ToSIA04:RF-HeatSink-H03B:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H03B_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H03B_TUpMon | .1
45 | Temperatura acima do set da Barra Dissipadora 04A | RA | ToSIA04 | RF | HeatSink | H04A | TUp | Mon | RA-ToSIA04:RF-HeatSink-H04A:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H04A_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H04A_TUpMon | .1
46 | Temperatura acima do set da Barra Dissipadora 04B | RA | ToSIA04 | RF | HeatSink | H04B | TUp | Mon | RA-ToSIA04:RF-HeatSink-H04B:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H04B_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H04B_TUpMon | .1
47 | Temperatura acima do set da Barra Dissipadora 05A | RA | ToSIA04 | RF | HeatSink | H05A | TUp | Mon | RA-ToSIA04:RF-HeatSink-H05A:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H05A_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H05A_TUpMon | .1
48 | Temperatura acima do set da Barra Dissipadora 05B | RA | ToSIA04 | RF | HeatSink | H05B | TUp | Mon | RA-ToSIA04:RF-HeatSink-H05B:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H05B_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H05B_TUpMon | .1
49 | Temperatura acima do set da Barra Dissipadora 06A | RA | ToSIA04 | RF | HeatSink | H06A | TUp | Mon | RA-ToSIA04:RF-HeatSink-H06A:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H06A_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H06A_TUpMon | .1
50 | Temperatura acima do set da Barra Dissipadora 06B | RA | ToSIA04 | RF | HeatSink | H06B | TUp | Mon | RA-ToSIA04:RF-HeatSink-H06B:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H06B_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H06B_TUpMon | .1
51 | Temperatura acima do set da Barra Dissipadora 07A | RA | ToSIA04 | RF | HeatSink | H07A | TUp | Mon | RA-ToSIA04:RF-HeatSink-H07A:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H07A_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H07A_TUpMon | .1
52 | Temperatura acima do set da Barra Dissipadora 07B | RA | ToSIA04 | RF | HeatSink | H07B | TUp | Mon | RA-ToSIA04:RF-HeatSink-H07B:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H07B_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H07B_TUpMon | .1
53 | Temperatura acima do set da Barra Dissipadora 08A | RA | ToSIA04 | RF | HeatSink | H08A | TUp | Mon | RA-ToSIA04:RF-HeatSink-H08A:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H08A_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H08A_TUpMon | .1
54 | Temperatura acima do set da Barra Dissipadora 08B | RA | ToSIA04 | RF | HeatSink | H08B | TUp | Mon | RA-ToSIA04:RF-HeatSink-H08B:TUp-Mon |  |  | RA_ToSIA04_RF_HeatSink_H08B_TUpMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H08B_TUpMon | .1
55 | Termostato da Barra Dissipadora 01A | RA | ToSIA04 | RF | HeatSink | H01A | Tms | Mon | RA-ToSIA04:RF-HeatSink-H01A:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H01A_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H01A_TmsMon | .1
56 | Termostato da Barra Dissipadora 01B | RA | ToSIA04 | RF | HeatSink | H01B | Tms | Mon | RA-ToSIA04:RF-HeatSink-H01B:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H01B_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H01B_TmsMon | .1
57 | Termostato da Barra Dissipadora 02A | RA | ToSIA04 | RF | HeatSink | H02A | Tms | Mon | RA-ToSIA04:RF-HeatSink-H02A:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H02A_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H02A_TmsMon | .1
58 | Termostato da Barra Dissipadora 02B | RA | ToSIA04 | RF | HeatSink | H02B | Tms | Mon | RA-ToSIA04:RF-HeatSink-H02B:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H02B_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H02B_TmsMon | .1
59 | Termostato da Barra Dissipadora 03A | RA | ToSIA04 | RF | HeatSink | H03A | Tms | Mon | RA-ToSIA04:RF-HeatSink-H03A:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H03A_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H03A_TmsMon | .1
60 | Termostato da Barra Dissipadora 03B | RA | ToSIA04 | RF | HeatSink | H03B | Tms | Mon | RA-ToSIA04:RF-HeatSink-H03B:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H03B_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H03B_TmsMon | .1
61 | Termostato da Barra Dissipadora 04A | RA | ToSIA04 | RF | HeatSink | H04A | Tms | Mon | RA-ToSIA04:RF-HeatSink-H04A:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H04A_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H04A_TmsMon | .1
62 | Termostato da Barra Dissipadora 04B | RA | ToSIA04 | RF | HeatSink | H04B | Tms | Mon | RA-ToSIA04:RF-HeatSink-H04B:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H04B_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H04B_TmsMon | .1
63 | Termostato da Barra Dissipadora 05A | RA | ToSIA04 | RF | HeatSink | H05A | Tms | Mon | RA-ToSIA04:RF-HeatSink-H05A:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H05A_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H05A_TmsMon | .1
64 | Termostato da Barra Dissipadora 05B | RA | ToSIA04 | RF | HeatSink | H05B | Tms | Mon | RA-ToSIA04:RF-HeatSink-H05B:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H05B_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H05B_TmsMon | .1
65 | Termostato da Barra Dissipadora 06A | RA | ToSIA04 | RF | HeatSink | H06A | Tms | Mon | RA-ToSIA04:RF-HeatSink-H06A:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H06A_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H06A_TmsMon | .1
66 | Termostato da Barra Dissipadora 06B | RA | ToSIA04 | RF | HeatSink | H06B | Tms | Mon | RA-ToSIA04:RF-HeatSink-H06B:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H06B_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H06B_TmsMon | .1
67 | Termostato da Barra Dissipadora 07A | RA | ToSIA04 | RF | HeatSink | H07A | Tms | Mon | RA-ToSIA04:RF-HeatSink-H07A:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H07A_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H07A_TmsMon | .1
68 | Termostato da Barra Dissipadora 07B | RA | ToSIA04 | RF | HeatSink | H07B | Tms | Mon | RA-ToSIA04:RF-HeatSink-H07B:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H07B_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H07B_TmsMon | .1
69 | Termostato da Barra Dissipadora 08A | RA | ToSIA04 | RF | HeatSink | H08A | Tms | Mon | RA-ToSIA04:RF-HeatSink-H08A:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H08A_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H08A_TmsMon | .1
70 | Termostato da Barra Dissipadora 08B | RA | ToSIA04 | RF | HeatSink | H08B | Tms | Mon | RA-ToSIA04:RF-HeatSink-H08B:Tms-Mon |  |  | RA_ToSIA04_RF_HeatSink_H08B_TmsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_HeatSink_H08B_TmsMon | .1
71 | Interlock Geral SSA 4 | RA | ToSIA04 | RF | SSAmpTower | - | Sts | Mon | RA-ToSIA04:RF-SSAmpTower:Sts-Mon |  |  | RA_ToSIA04_RF_SSAmpTower_StsMon | Digital | Input |  |  |  | RA_ToSIA04_RF_SSAmpTower_StsMon | .1
72 | Rotâmetro Torre 04 do Anel | RA | ToSIA04 | RF | SSAmpTower | - | HdFlwRt | Mon | RA-ToSIA04:RF-SSAmpTower:HdFlwRt-Mon |  |  | RA_ToSIA04_RF_SSAmpTower_HdFlwRtMon | Digital | Input |  |  |  | RA_ToSIA04_RF_SSAmpTower_HdFlwRtMon | .1
73 | 48V das Fontes TDK Torre 04 Off | RA | ToSIA04 | RF | TDKSource | - | PwrDCDsbl | Sel | RA-ToSIA04:RF-TDKSource:PwrDCDsbl-Sel |  |  | RA_ToSIA04_RF_TDKSource_PwrDCDsblSel | Digital | Control |  |  |  | RA_ToSIA04_RF_TDKSource_PwrDCDsblSel | .1 |  | 0.5
74 | 48V das Fontes TDK Torre 04 On | RA | ToSIA04 | RF | TDKSource | - | PwrDCEnbl | Sel | RA-ToSIA04:RF-TDKSource:PwrDCEnbl-Sel |  |  | RA_ToSIA04_RF_TDKSource_PwrDCEnblSel | Digital | Control |  |  |  | RA_ToSIA04_RF_TDKSource_PwrDCEnblSel | .1 |  | 0.5
75 | 48V das Fontes TDK Torre 04 Status | RA | ToSIA04 | RF | TDKSource | - | PwrDC | Sts | RA-ToSIA04:RF-TDKSource:PwrDC-Sts |  |  | RA_ToSIA04_RF_TDKSource_PwrDCSts | Digital | Input |  |  |  | RA_ToSIA04_RF_TDKSource_PwrDCSts | .1
76 | Falha Ac Mini Rack 1 Torre 4 | RA | ToSIA04 | RF | TDKSource | R1 | StsAC | Mon | RA-ToSIA04:RF-TDKSource-R1:StsAC-Mon |  |  | RA_ToSIA04_RF_TDKSource_R1_StsACMon | Digital | Input |  |  |  | RA_ToSIA04_RF_TDKSource_R1_StsACMon | .1
77 | Falha Ac Mini Rack 2 Torre 4 | RA | ToSIA04 | RF | TDKSource | R2 | StsAC | Mon | RA-ToSIA04:RF-TDKSource-R2:StsAC-Mon |  |  | RA_ToSIA04_RF_TDKSource_R2_StsACMon | Digital | Input |  |  |  | RA_ToSIA04_RF_TDKSource_R2_StsACMon | .1
78 | Falha Ac Mini Rack 3 Torre 4 | RA | ToSIA04 | RF | TDKSource | R3 | StsAC | Mon | RA-ToSIA04:RF-TDKSource-R3:StsAC-Mon |  |  | RA_ToSIA04_RF_TDKSource_R3_StsACMon | Digital | Input |  |  |  | RA_ToSIA04_RF_TDKSource_R3_StsACMon | .1
79 | Falha Ac Mini Rack 4 Torre 4 | RA | ToSIA04 | RF | TDKSource | R4 | StsAC | Mon | RA-ToSIA04:RF-TDKSource-R4:StsAC-Mon |  |  | RA_ToSIA04_RF_TDKSource_R4_StsACMon | Digital | Input |  |  |  | RA_ToSIA04_RF_TDKSource_R4_StsACMon | .1
80 | Interlock externo do CLP para Painel Torre 04 (Saída) | RA | ToSIA04 | RF | Intlk | - | IntlkACPanel | Mon | RA-ToSIA04:RF-Intlk:IntlkACPanel-Mon |  |  | RA_ToSIA04_RF_Intlk_IntlkACPanelMon | Digital | Input |  |  |  | RA_ToSIA04_RF_Intlk_IntlkACPanelMon | .1
81 | Torre 4 Enbl | RA | ToSIA04 | RF | SSAmpTower | - | Enbl | Sel | RA-ToSIA04:RF-SSAmpTower:Enbl-Sel |  |  | RA_ToSIA04_RF_SSAmpTower_EnblSel | Digital | Control |  |  |  | RA_ToSIA04_RF_SSAmpTower_EnblSel | .1
82 | Torre 4 Enbl Sts | RA | ToSIA04 | RF | SSAmpTower | - | Enbl | Sts | RA-ToSIA04:RF-SSAmpTower:Enbl-Sts |  |  | RA_ToSIA04_RF_SSAmpTower_EnblSts | Digital | Input |  |  |  | RA_ToSIA04_RF_SSAmpTower_EnblSts | .1
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
[9 empty] | -:--:- |  |  | _____ | [5 empty] | _____
83 | Falha Fusível eletrônico | RA | ToSIA03 | RF | CtrlPanel | - | PwrSts | Mon | RA-ToSIA03:RF-CtrlPanel:PwrSts-Mon | N/A | N/A | Memorias[0].0 | Digital | Input | N/A | N/A |  | Memorias[0].0 | .1
84 | Falha fonte 24VDC | RA | ToSIA03 | RF | ACPanel | - | StsPos24V | Mon | RA-ToSIA03:RF-ACPanel:StsPos24V-Mon | N/A | N/A | Memorias[0].1 | Digital | Input | N/A | N/A |  | Memorias[0].1 | .1
85 | Medida Potencia incidente de entrada | RA | ToSIA03 | RF | SSAmpTower | - | PwrFwdIn | Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdIn-Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdInUpperLimit-Cte | N/A | Remote_01_Torre_Teste:5:I.Ch00.Data | Analog | Input | Real[4] | N/A |  | Remote_01_Torre_Teste:5:I.Ch00.Data | .1 | 2 |  | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0
86 | Medida Potencia Refletida de entrada | RA | ToSIA03 | RF | SSAmpTower | - | PwrRevIn | Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevIn-Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevInUpperLimit-Cte | N/A | Remote_01_Torre_Teste:5:I.Ch01.Data | Analog | Input | Real[5] | N/A |  | Remote_01_Torre_Teste:5:I.Ch01.Data | .1 | 2 |  | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0
87 | Medida Potencia incidente de saída | RA | ToSIA03 | RF | SSAmpTower | - | PwrFwdOut | Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdOut-Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdOutUpperLimit-Cte | N/A | Remote_01_Torre_Teste:5:I.Ch02.Data | Analog | Input | Real[6] | N/A |  | Remote_01_Torre_Teste:5:I.Ch02.Data | .1 | 2 |  | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0
88 | Medida Potencia refletida de saída | RA | ToSIA03 | RF | SSAmpTower | - | PwrRevOut | Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevOut-Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevOutUpperLimit-Cte | N/A | Remote_01_Torre_Teste:5:I.Ch03.Data | Analog | Input | Real[7] | N/A |  | Remote_01_Torre_Teste:5:I.Ch03.Data | .1 | 2 |  | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0
89 | Falha Pot Incidente de entrada | RA | ToSIA03 | RF | SSAmpTower | - | PwrFwdInSts | Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdInSts-Mon | N/A | N/A | Falha_Pot_RF.0 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.0 | .1
90 | Falha Pot Refletida de entrada | RA | ToSIA03 | RF | SSAmpTower | - | PwrRevInSts | Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevInSts-Mon | N/A | N/A | Falha_Pot_RF.1 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.1 | .1
91 | Falha Pot Incidente de Saída | RA | ToSIA03 | RF | SSAmpTower | - | PwrFwdOutSts | Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdOutSts-Mon | N/A | N/A | Falha_Pot_RF.2 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.2 | .1
92 | Falha Pot Refletida de Saída | RA | ToSIA03 | RF | SSAmpTower | - | PwrRevOutSts | Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevOutSts-Mon | N/A | N/A | Falha_Pot_RF.3 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.3 | .1
93 | Falha Pot RF torre 03 | RA | ToSIA03 | RF | SSAmpTower | - | RFPwrSts | Mon | RA-ToSIA03:RF-SSAmpTower:RFPwrSts-Mon | N/A | N/A | Falha_Pot_RF.4 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.4 | .1
94 | Hablita coaxial switch torre 03 | RA | ToSIA03 | RF | CtrlPanel | - | PINSwEnbl | Cmd | RA-ToSIA03:RF-CtrlPanel:PINSwEnbl-Cmd | N/A | N/A | Memorias[3].16 | Digital | Control | N/A | N/A |  | Memorias[3].16 | .1 |  | 0.5
95 | Desabilita coaxial switch torre 03 | RA | ToSIA03 | RF | CtrlPanel | - | PINSwDsbl | Cmd | RA-ToSIA03:RF-CtrlPanel:PINSwDsbl-Cmd | N/A | N/A | Memorias[3].18 | Digital | Control | N/A | N/A |  | Memorias[3].18 | .1 |  | 0.5
96 | Status coaxial switch torre 03 | RA | ToSIA03 | RF | CtrlPanel | - | PINSwSts | Mon | RA-ToSIA03:RF-CtrlPanel:PINSwSts-Mon | N/A | N/A | Remote_01_Torre_Teste:8:O.Pt06.Data | Digital | Output | N/A | N/A |  | Remote_01_Torre_Teste:8:O.Pt06.Data | .1
97 | Horímetro Torre 03 | RA | ToSIA03 | RF | SSAmpTower | - | RunHour | Mon | RA-ToSIA03:RF-SSAmpTower:RunHour-Mon | N/A | N/A | Real[10] | Analog | Input | N/A | N/A | h | Real[10] | .1
98 | Falha Rotâmetro Carga 80kw | RA | ToSIA04 | RF | SSAmpTower | - | LoadHdFlwRt | Mon | RA-ToSIA04:RF-SSAmpTower:LoadHdFlwRt-Mon | N/A | N/A | Memorias[1].20 | Digital | Input | N/A | N/A |  | Memorias[1].20 | .1

## SSAmp Tower 04 Multi ABB
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Corrente de Fase 1 | RA | ToSIA04 | RF | ACPanel | - | PhsCurrent1 | Mon | RA-ToSIA04:RF-ACPanel:PhsCurrent1-Mon | N/A | N/A | RA_ToSIA04_RF_ACPanel_PhsCurrent1Mon | Digital | Input | N/A | N/A |  | RA_ToSIA04_RF_ACPanel_PhsCurrent1Mon | .1
2 | Corrente de Fase 2 | RA | ToSIA04 | RF | ACPanel | - | PhsCurrent2 | Mon | RA-ToSIA04:RF-ACPanel:PhsCurrent2-Mon | N/A | N/A | RA_ToSIA04_RF_ACPanel_PhsCurrent2Mon | Digital | Input | N/A | N/A |  | RA_ToSIA04_RF_ACPanel_PhsCurrent2Mon | .1
3 | Corrente de Fase 3 | RA | ToSIA04 | RF | ACPanel | - | PhsCurrent3 | Mon | RA-ToSIA04:RF-ACPanel:PhsCurrent3-Mon | RA-ToSIA04:RF-ACPanel:PhsCurrent3UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:PhsCurrent3LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_PhsCurrent3Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_PhsCurrent3Mon | .5 | 2
4 | Tensão Fase 1 | RA | ToSIA04 | RF | ACPanel | - | PhsVoltage1 | Mon | RA-ToSIA04:RF-ACPanel:PhsVoltage1-Mon | RA-ToSIA04:RF-ACPanel:PhsVoltage1UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:PhsVoltage1LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_PhsVoltage1Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_PhsVoltage1Mon | .5 | 2
5 | Tensão Fase 2 | RA | ToSIA04 | RF | ACPanel | - | PhsVoltage2 | Mon | RA-ToSIA04:RF-ACPanel:PhsVoltage2-Mon | RA-ToSIA04:RF-ACPanel:PhsVoltage2UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:PhsVoltage2LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_PhsVoltage2Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_PhsVoltage2Mon | .5 | 2
6 | Tensão Fase 3 | RA | ToSIA04 | RF | ACPanel | - | PhsVoltage3 | Mon | RA-ToSIA04:RF-ACPanel:PhsVoltage3-Mon | RA-ToSIA04:RF-ACPanel:PhsVoltage3UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:PhsVoltage3LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_PhsVoltage3Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_PhsVoltage3Mon | .5 | 2
7 | Tensão de linha 12 | RA | ToSIA04 | RF | ACPanel | - | LineVoltage12 | Mon | RA-ToSIA04:RF-ACPanel:LineVoltage12-Mon | RA-ToSIA04:RF-ACPanel:LineVoltage12UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:LineVoltage12LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_LineVoltage12Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_LineVoltage12Mon | .5 | 2
8 | Tensão de linha 13 | RA | ToSIA04 | RF | ACPanel | - | LineVoltage13 | Mon | RA-ToSIA04:RF-ACPanel:LineVoltage13-Mon | RA-ToSIA04:RF-ACPanel:LineVoltage13UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:LineVoltage13LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_LineVoltage13Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_LineVoltage13Mon | .5 | 2
9 | Tensão de linha 23 | RA | ToSIA04 | RF | ACPanel | - | LineVoltage23 | Mon | RA-ToSIA04:RF-ACPanel:LineVoltage23-Mon | RA-ToSIA04:RF-ACPanel:LineVoltage23UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:LineVoltage23LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_LineVoltage23Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_LineVoltage23Mon | .5 | 2
10 | Potência S | RA | ToSIA04 | RF | ACPanel | - | PwrS | Mon | RA-ToSIA04:RF-ACPanel:PwrS-Mon | RA-ToSIA04:RF-ACPanel:PwrSUpperLimit-Cte | RA-ToSIA04:RF-ACPanel:PwrSLowerLimit-Cte | RA_ToSIA04_RF_ACPanel_PwrSMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_PwrSMon | .5 | 2
11 | Potencia P | RA | ToSIA04 | RF | ACPanel | - | PwrP | Mon | RA-ToSIA04:RF-ACPanel:PwrP-Mon | RA-ToSIA04:RF-ACPanel:PwrPUpperLimit-Cte | RA-ToSIA04:RF-ACPanel:PwrPLowerLimit-Cte | RA_ToSIA04_RF_ACPanel_PwrPMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_PwrPMon | .5 | 2
12 | Potência Q | RA | ToSIA04 | RF | ACPanel | - | PwrQ | Mon | RA-ToSIA04:RF-ACPanel:PwrQ-Mon | RA-ToSIA04:RF-ACPanel:PwrQUpperLimit-Cte | RA-ToSIA04:RF-ACPanel:PwrQLowerLimit-Cte | RA_ToSIA04_RF_ACPanel_PwrQMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_PwrQMon | .5 | 2
13 | Fator de potência | RA | ToSIA04 | RF | ACPanel | - | PwrFactor | Mon | RA-ToSIA04:RF-ACPanel:PwrFactor-Mon | RA-ToSIA04:RF-ACPanel:PwrFactorUpperLimit-Cte | RA-ToSIA04:RF-ACPanel:PwrFactorLowerLimit-Cte | RA_ToSIA04_RF_ACPanel_PwrFactorMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_PwrFactorMon | .5 | 2
14 | THD 1 | RA | ToSIA04 | RF | ACPanel | - | THD1 | Mon | RA-ToSIA04:RF-ACPanel:THD1-Mon | RA-ToSIA04:RF-ACPanel:THD1UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:THD1LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_THD1Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_THD1Mon | .5 | 2
15 | THD 2 | RA | ToSIA04 | RF | ACPanel | - | THD2 | Mon | RA-ToSIA04:RF-ACPanel:THD2-Mon | RA-ToSIA04:RF-ACPanel:THD2UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:THD2LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_THD2Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_THD2Mon | .5 | 2
16 | THD 3 | RA | ToSIA04 | RF | ACPanel | - | THD3 | Mon | RA-ToSIA04:RF-ACPanel:THD3-Mon | RA-ToSIA04:RF-ACPanel:THD3UpperLimit-Cte | RA-ToSIA04:RF-ACPanel:THD3LowerLimit-Cte | RA_ToSIA04_RF_ACPanel_THD3Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_THD3Mon | .5 | 2
17 | Corrente Neutro | RA | ToSIA04 | RF | ACPanel | - | CurrentN | Mon | RA-ToSIA04:RF-ACPanel:CurrentN-Mon | RA-ToSIA04:RF-ACPanel:CurrentNUpperLimit-Cte | RA-ToSIA04:RF-ACPanel:CurrentNLowerLimit-Cte | RA_ToSIA04_RF_ACPanel_CurrentNMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_CurrentNMon | .5 | 2
18 | Frequencia | RA | ToSIA04 | RF | ACPanel | - | Freq | Mon | RA-ToSIA04:RF-ACPanel:Freq-Mon | RA-ToSIA04:RF-ACPanel:FreqUpperLimit-Cte | RA-ToSIA04:RF-ACPanel:FreqLowerLimit-Cte | RA_ToSIA04_RF_ACPanel_FreqMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA04_RF_ACPanel_FreqMon | .5 | 2

## SSAmp Tower 03 CLP
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec | Cmd Duration | PV Conversion | Upper Limit Conversion | Lower Limit Conversion
1 | AC da Torre 03 do Anel Status | RA | ToSIA03 | RF | ACPanel | - | PwrACOp | Mon | RA-ToSIA03:RF-ACPanel:PwrACOp-Mon | N/A | N/A | Memorias[5].16 | Digital | Input | N/A | N/A |  | Memorias[5].16 | .1
2 | AC das Fontes TDK Torre 03 Off | RA | ToSIA03 | RF | ACPanel | - | PwrACDsbl | Sel | RA-ToSIA03:RF-ACPanel:PwrACDsbl-Sel | N/A | N/A | Memorias[2].28 | Digital | Control | N/A | N/A |  | Memorias[2].28 | .1 |  | 0.5
3 | AC das Fontes TDK Torre 03 On | RA | ToSIA03 | RF | ACPanel | - | PwrACEnbl | Sel | RA-ToSIA03:RF-ACPanel:PwrACEnbl-Sel | N/A | N/A | Memorias[3].0 | Digital | Control | N/A | N/A |  | Memorias[3].0 | .1 |  | 0.5
4 | AC das Fontes TDK Torre 03 Status | RA | ToSIA03 | RF | ACPanel | - | PwrAC | Sts | RA-ToSIA03:RF-ACPanel:PwrAC-Sts | N/A | N/A | Memorias[2].24 | Digital | Output | N/A | N/A |  | Memorias[2].24 | .1
5 | Falta de Fase do Painel Torre 03 do Anel | RA | ToSIA03 | RF | ACPanel | - | PhsFlt | Mon | RA-ToSIA03:RF-ACPanel:PhsFlt-Mon | N/A | N/A | Memorias[0].3 | Digital | Input | N/A | N/A |  | Memorias[0].3 | .1
6 | Interlock externo do Painel Torre 03 | RA | ToSIA03 | RF | ACPanel | - | Intlk | Mon | RA-ToSIA03:RF-ACPanel:Intlk-Mon | N/A | N/A | Memorias[0].2 | Digital | Input | N/A | N/A |  | Memorias[0].2 | .1
7 | PT-100 da Barra Dissipadora 01A | RA | ToSIA03 | RF | HeatSink | H01A | T | Mon | RA-ToSIA03:RF-HeatSink-H01A:T-Mon | RA-ToSIA03:RF-HeatSink-H01A:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H01A:TLowerLimit-Cte | Remote_01_Torre_Teste:1:I.Ch00.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:1:I.Ch00.Data | .5 | 2 |  | pv | pv | pv
8 | PT-100 da Barra Dissipadora 01B | RA | ToSIA03 | RF | HeatSink | H01B | T | Mon | RA-ToSIA03:RF-HeatSink-H01B:T-Mon | RA-ToSIA03:RF-HeatSink-H01B:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H01B:TLowerLimit-Cte | Remote_01_Torre_Teste:1:I.Ch01.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:1:I.Ch01.Data | .5 | 2 |  | pv | pv | pv
9 | PT-100 da Barra Dissipadora 02A | RA | ToSIA03 | RF | HeatSink | H02A | T | Mon | RA-ToSIA03:RF-HeatSink-H02A:T-Mon | RA-ToSIA03:RF-HeatSink-H02A:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H02A:TLowerLimit-Cte | Remote_01_Torre_Teste:1:I.Ch02.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:1:I.Ch02.Data | .5 | 2 |  | pv | pv | pv
10 | PT-100 da Barra Dissipadora 02B | RA | ToSIA03 | RF | HeatSink | H02B | T | Mon | RA-ToSIA03:RF-HeatSink-H02B:T-Mon | RA-ToSIA03:RF-HeatSink-H02B:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H02B:TLowerLimit-Cte | Remote_01_Torre_Teste:1:I.Ch03.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:1:I.Ch03.Data | .5 | 2 |  | pv | pv | pv
11 | PT-100 da Barra Dissipadora 03A | RA | ToSIA03 | RF | HeatSink | H03A | T | Mon | RA-ToSIA03:RF-HeatSink-H03A:T-Mon | RA-ToSIA03:RF-HeatSink-H03A:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H03A:TLowerLimit-Cte | PT100_B_03A | Analog | Input | Real[0] | Real[1] | C | PT100_B_03A | .5 | 2 |  | pv | pv | pv
12 | PT-100 da Barra Dissipadora 03B | RA | ToSIA03 | RF | HeatSink | H03B | T | Mon | RA-ToSIA03:RF-HeatSink-H03B:T-Mon | RA-ToSIA03:RF-HeatSink-H03B:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H03B:TLowerLimit-Cte | Remote_01_Torre_Teste:2:I.Ch01.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:2:I.Ch01.Data | .5 | 2 |  | pv | pv | pv
13 | PT-100 da Barra Dissipadora 04A | RA | ToSIA03 | RF | HeatSink | H04A | T | Mon | RA-ToSIA03:RF-HeatSink-H04A:T-Mon | RA-ToSIA03:RF-HeatSink-H04A:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H04A:TLowerLimit-Cte | Remote_01_Torre_Teste:2:I.Ch02.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:2:I.Ch02.Data | .5 | 2 |  | pv | pv | pv
14 | PT-100 da Barra Dissipadora 04B | RA | ToSIA03 | RF | HeatSink | H04B | T | Mon | RA-ToSIA03:RF-HeatSink-H04B:T-Mon | RA-ToSIA03:RF-HeatSink-H04B:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H04B:TLowerLimit-Cte | Remote_01_Torre_Teste:2:I.Ch03.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:2:I.Ch03.Data | .5 | 2 |  | pv | pv | pv
15 | PT-100 da Barra Dissipadora 05A | RA | ToSIA03 | RF | HeatSink | H05A | T | Mon | RA-ToSIA03:RF-HeatSink-H05A:T-Mon | RA-ToSIA03:RF-HeatSink-H05A:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H05A:TLowerLimit-Cte | PT100_B_05A | Analog | Input | Real[0] | Real[1] | C | PT100_B_05A | .5 | 2 |  | pv | pv | pv
16 | PT-100 da Barra Dissipadora 05B | RA | ToSIA03 | RF | HeatSink | H05B | T | Mon | RA-ToSIA03:RF-HeatSink-H05B:T-Mon | RA-ToSIA03:RF-HeatSink-H05B:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H05B:TLowerLimit-Cte | Remote_01_Torre_Teste:3:I.Ch01.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:3:I.Ch01.Data | .5 | 2 |  | pv | pv | pv
17 | PT-100 da Barra Dissipadora 06A | RA | ToSIA03 | RF | HeatSink | H06A | T | Mon | RA-ToSIA03:RF-HeatSink-H06A:T-Mon | RA-ToSIA03:RF-HeatSink-H06A:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H06A:TLowerLimit-Cte | Remote_01_Torre_Teste:3:I.Ch02.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:3:I.Ch02.Data | .5 | 2 |  | pv | pv | pv
18 | PT-100 da Barra Dissipadora 06B | RA | ToSIA03 | RF | HeatSink | H06B | T | Mon | RA-ToSIA03:RF-HeatSink-H06B:T-Mon | RA-ToSIA03:RF-HeatSink-H06B:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H06B:TLowerLimit-Cte | Remote_01_Torre_Teste:3:I.Ch03.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:3:I.Ch03.Data | .5 | 2 |  | pv | pv | pv
19 | PT-100 da Barra Dissipadora 07A | RA | ToSIA03 | RF | HeatSink | H07A | T | Mon | RA-ToSIA03:RF-HeatSink-H07A:T-Mon | RA-ToSIA03:RF-HeatSink-H07A:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H07A:TLowerLimit-Cte | PT100_B_07A | Analog | Input | Real[0] | Real[1] | C | PT100_B_07A | .5 | 2 |  | pv | pv | pv
20 | PT-100 da Barra Dissipadora 07B | RA | ToSIA03 | RF | HeatSink | H07B | T | Mon | RA-ToSIA03:RF-HeatSink-H07B:T-Mon | RA-ToSIA03:RF-HeatSink-H07B:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H07B:TLowerLimit-Cte | Remote_01_Torre_Teste:4:I.Ch01.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:4:I.Ch01.Data | .5 | 2 |  | pv | pv | pv
21 | PT-100 da Barra Dissipadora 08A | RA | ToSIA03 | RF | HeatSink | H08A | T | Mon | RA-ToSIA03:RF-HeatSink-H08A:T-Mon | RA-ToSIA03:RF-HeatSink-H08A:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H08A:TLowerLimit-Cte | Remote_01_Torre_Teste:4:I.Ch02.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:4:I.Ch02.Data | .5 | 2 |  | pv | pv | pv
22 | PT-100 da Barra Dissipadora 08B | RA | ToSIA03 | RF | HeatSink | H08B | T | Mon | RA-ToSIA03:RF-HeatSink-H08B:T-Mon | RA-ToSIA03:RF-HeatSink-H08B:TUpperLimit-Cte | RA-ToSIA03:RF-HeatSink-H08B:TLowerLimit-Cte | Remote_01_Torre_Teste:4:I.Ch03.Data | Analog | Input | Real[0] | Real[1] | C | Remote_01_Torre_Teste:4:I.Ch03.Data | .5 | 2 |  | pv | pv | pv
23 | Temperatura abaixo do set da Barra Dissipadora 01A | RA | ToSIA03 | RF | HeatSink | H01A | TDown | Mon | RA-ToSIA03:RF-HeatSink-H01A:TDown-Mon | N/A | N/A | Memorias[1].4 | Digital | Input | N/A | N/A |  | Memorias[1].4 | .1
24 | Temperatura abaixo do set da Barra Dissipadora 01B | RA | ToSIA03 | RF | HeatSink | H01B | TDown | Mon | RA-ToSIA03:RF-HeatSink-H01B:TDown-Mon | N/A | N/A | Memorias[1].5 | Digital | Input | N/A | N/A |  | Memorias[1].5 | .1
25 | Temperatura abaixo do set da Barra Dissipadora 02A | RA | ToSIA03 | RF | HeatSink | H02A | TDown | Mon | RA-ToSIA03:RF-HeatSink-H02A:TDown-Mon | N/A | N/A | Memorias[1].6 | Digital | Input | N/A | N/A |  | Memorias[1].6 | .1
26 | Temperatura abaixo do set da Barra Dissipadora 02B | RA | ToSIA03 | RF | HeatSink | H02B | TDown | Mon | RA-ToSIA03:RF-HeatSink-H02B:TDown-Mon | N/A | N/A | Memorias[1].7 | Digital | Input | N/A | N/A |  | Memorias[1].7 | .1
27 | Temperatura abaixo do set da Barra Dissipadora 03A | RA | ToSIA03 | RF | HeatSink | H03A | TDown | Mon | RA-ToSIA03:RF-HeatSink-H03A:TDown-Mon | N/A | N/A | Memorias[1].8 | Digital | Input | N/A | N/A |  | Memorias[1].8 | .1
28 | Temperatura abaixo do set da Barra Dissipadora 03B | RA | ToSIA03 | RF | HeatSink | H03B | TDown | Mon | RA-ToSIA03:RF-HeatSink-H03B:TDown-Mon | N/A | N/A | Memorias[1].9 | Digital | Input | N/A | N/A |  | Memorias[1].9 | .1
29 | Temperatura abaixo do set da Barra Dissipadora 04A | RA | ToSIA03 | RF | HeatSink | H04A | TDown | Mon | RA-ToSIA03:RF-HeatSink-H04A:TDown-Mon | N/A | N/A | Memorias[1].10 | Digital | Input | N/A | N/A |  | Memorias[1].10 | .1
30 | Temperatura abaixo do set da Barra Dissipadora 04B | RA | ToSIA03 | RF | HeatSink | H04B | TDown | Mon | RA-ToSIA03:RF-HeatSink-H04B:TDown-Mon | N/A | N/A | Memorias[1].11 | Digital | Input | N/A | N/A |  | Memorias[1].11 | .1
31 | Temperatura abaixo do set da Barra Dissipadora 05A | RA | ToSIA03 | RF | HeatSink | H05A | TDown | Mon | RA-ToSIA03:RF-HeatSink-H05A:TDown-Mon | N/A | N/A | Memorias[1].12 | Digital | Input | N/A | N/A |  | Memorias[1].12 | .1
32 | Temperatura abaixo do set da Barra Dissipadora 05B | RA | ToSIA03 | RF | HeatSink | H05B | TDown | Mon | RA-ToSIA03:RF-HeatSink-H05B:TDown-Mon | N/A | N/A | Memorias[1].13 | Digital | Input | N/A | N/A |  | Memorias[1].13 | .1
33 | Temperatura abaixo do set da Barra Dissipadora 06A | RA | ToSIA03 | RF | HeatSink | H06A | TDown | Mon | RA-ToSIA03:RF-HeatSink-H06A:TDown-Mon | N/A | N/A | Memorias[1].14 | Digital | Input | N/A | N/A |  | Memorias[1].14 | .1
34 | Temperatura abaixo do set da Barra Dissipadora 06B | RA | ToSIA03 | RF | HeatSink | H06B | TDown | Mon | RA-ToSIA03:RF-HeatSink-H06B:TDown-Mon | N/A | N/A | Memorias[1].15 | Digital | Input | N/A | N/A |  | Memorias[1].15 | .1
35 | Temperatura abaixo do set da Barra Dissipadora 07A | RA | ToSIA03 | RF | HeatSink | H07A | TDown | Mon | RA-ToSIA03:RF-HeatSink-H07A:TDown-Mon | N/A | N/A | Memorias[1].16 | Digital | Input | N/A | N/A |  | Memorias[1].16 | .1
36 | Temperatura abaixo do set da Barra Dissipadora 07B | RA | ToSIA03 | RF | HeatSink | H07B | TDown | Mon | RA-ToSIA03:RF-HeatSink-H07B:TDown-Mon | N/A | N/A | Memorias[1].17 | Digital | Input | N/A | N/A |  | Memorias[1].17 | .1
37 | Temperatura abaixo do set da Barra Dissipadora 08A | RA | ToSIA03 | RF | HeatSink | H08A | TDown | Mon | RA-ToSIA03:RF-HeatSink-H08A:TDown-Mon | N/A | N/A | Memorias[1].18 | Digital | Input | N/A | N/A |  | Memorias[1].18 | .1
38 | Temperatura abaixo do set da Barra Dissipadora 08B | RA | ToSIA03 | RF | HeatSink | H08B | TDown | Mon | RA-ToSIA03:RF-HeatSink-H08B:TDown-Mon | N/A | N/A | Memorias[1].19 | Digital | Input | N/A | N/A |  | Memorias[1].19 | .1
39 | Temperatura acima do set da Barra Dissipadora 01A | RA | ToSIA03 | RF | HeatSink | H01A | TUp | Mon | RA-ToSIA03:RF-HeatSink-H01A:TUp-Mon | N/A | N/A | Memorias[0].20 | Digital | Input | N/A | N/A |  | Memorias[0].20 | .1
40 | Temperatura acima do set da Barra Dissipadora 01B | RA | ToSIA03 | RF | HeatSink | H01B | TUp | Mon | RA-ToSIA03:RF-HeatSink-H01B:TUp-Mon | N/A | N/A | Memorias[0].21 | Digital | Input | N/A | N/A |  | Memorias[0].21 | .1
41 | Temperatura acima do set da Barra Dissipadora 02A | RA | ToSIA03 | RF | HeatSink | H02A | TUp | Mon | RA-ToSIA03:RF-HeatSink-H02A:TUp-Mon | N/A | N/A | Memorias[0].22 | Digital | Input | N/A | N/A |  | Memorias[0].22 | .1
42 | Temperatura acima do set da Barra Dissipadora 02B | RA | ToSIA03 | RF | HeatSink | H02B | TUp | Mon | RA-ToSIA03:RF-HeatSink-H02B:TUp-Mon | N/A | N/A | Memorias[0].23 | Digital | Input | N/A | N/A |  | Memorias[0].23 | .1
43 | Temperatura acima do set da Barra Dissipadora 03A | RA | ToSIA03 | RF | HeatSink | H03A | TUp | Mon | RA-ToSIA03:RF-HeatSink-H03A:TUp-Mon | N/A | N/A | Memorias[0].24 | Digital | Input | N/A | N/A |  | Memorias[0].24 | .1
44 | Temperatura acima do set da Barra Dissipadora 03B | RA | ToSIA03 | RF | HeatSink | H03B | TUp | Mon | RA-ToSIA03:RF-HeatSink-H03B:TUp-Mon | N/A | N/A | Memorias[0].25 | Digital | Input | N/A | N/A |  | Memorias[0].25 | .1
45 | Temperatura acima do set da Barra Dissipadora 04A | RA | ToSIA03 | RF | HeatSink | H04A | TUp | Mon | RA-ToSIA03:RF-HeatSink-H04A:TUp-Mon | N/A | N/A | Memorias[0].26 | Digital | Input | N/A | N/A |  | Memorias[0].26 | .1
46 | Temperatura acima do set da Barra Dissipadora 04B | RA | ToSIA03 | RF | HeatSink | H04B | TUp | Mon | RA-ToSIA03:RF-HeatSink-H04B:TUp-Mon | N/A | N/A | Memorias[0].27 | Digital | Input | N/A | N/A |  | Memorias[0].27 | .1
47 | Temperatura acima do set da Barra Dissipadora 05A | RA | ToSIA03 | RF | HeatSink | H05A | TUp | Mon | RA-ToSIA03:RF-HeatSink-H05A:TUp-Mon | N/A | N/A | Memorias[0].28 | Digital | Input | N/A | N/A |  | Memorias[0].28 | .1
48 | Temperatura acima do set da Barra Dissipadora 05B | RA | ToSIA03 | RF | HeatSink | H05B | TUp | Mon | RA-ToSIA03:RF-HeatSink-H05B:TUp-Mon | N/A | N/A | Memorias[0].29 | Digital | Input | N/A | N/A |  | Memorias[0].29 | .1
49 | Temperatura acima do set da Barra Dissipadora 06A | RA | ToSIA03 | RF | HeatSink | H06A | TUp | Mon | RA-ToSIA03:RF-HeatSink-H06A:TUp-Mon | N/A | N/A | Memorias[0].30 | Digital | Input | N/A | N/A |  | Memorias[0].30 | .1
50 | Temperatura acima do set da Barra Dissipadora 06B | RA | ToSIA03 | RF | HeatSink | H06B | TUp | Mon | RA-ToSIA03:RF-HeatSink-H06B:TUp-Mon | N/A | N/A | Memorias[0].31 | Digital | Input | N/A | N/A |  | Memorias[0].31 | .1
51 | Temperatura acima do set da Barra Dissipadora 07A | RA | ToSIA03 | RF | HeatSink | H07A | TUp | Mon | RA-ToSIA03:RF-HeatSink-H07A:TUp-Mon | N/A | N/A | Memorias[1].0 | Digital | Input | N/A | N/A |  | Memorias[1].0 | .1
52 | Temperatura acima do set da Barra Dissipadora 07B | RA | ToSIA03 | RF | HeatSink | H07B | TUp | Mon | RA-ToSIA03:RF-HeatSink-H07B:TUp-Mon | N/A | N/A | Memorias[1].1 | Digital | Input | N/A | N/A |  | Memorias[1].1 | .1
53 | Temperatura acima do set da Barra Dissipadora 08A | RA | ToSIA03 | RF | HeatSink | H08A | TUp | Mon | RA-ToSIA03:RF-HeatSink-H08A:TUp-Mon | N/A | N/A | Memorias[1].2 | Digital | Input | N/A | N/A |  | Memorias[1].2 | .1
54 | Temperatura acima do set da Barra Dissipadora 08B | RA | ToSIA03 | RF | HeatSink | H08B | TUp | Mon | RA-ToSIA03:RF-HeatSink-H08B:TUp-Mon | N/A | N/A | Memorias[1].3 | Digital | Input | N/A | N/A |  | Memorias[1].3 | .1
55 | Termostato da Barra Dissipadora 01A | RA | ToSIA03 | RF | HeatSink | H01A | Tms | Mon | RA-ToSIA03:RF-HeatSink-H01A:Tms-Mon | N/A | N/A | Memorias[0].4 | Digital | Input | N/A | N/A |  | Memorias[0].4 | .1
56 | Termostato da Barra Dissipadora 01B | RA | ToSIA03 | RF | HeatSink | H01B | Tms | Mon | RA-ToSIA03:RF-HeatSink-H01B:Tms-Mon | N/A | N/A | Memorias[0].5 | Digital | Input | N/A | N/A |  | Memorias[0].5 | .1
57 | Termostato da Barra Dissipadora 02A | RA | ToSIA03 | RF | HeatSink | H02A | Tms | Mon | RA-ToSIA03:RF-HeatSink-H02A:Tms-Mon | N/A | N/A | Memorias[0].6 | Digital | Input | N/A | N/A |  | Memorias[0].6 | .1
58 | Termostato da Barra Dissipadora 02B | RA | ToSIA03 | RF | HeatSink | H02B | Tms | Mon | RA-ToSIA03:RF-HeatSink-H02B:Tms-Mon | N/A | N/A | Memorias[0].7 | Digital | Input | N/A | N/A |  | Memorias[0].7 | .1
59 | Termostato da Barra Dissipadora 03A | RA | ToSIA03 | RF | HeatSink | H03A | Tms | Mon | RA-ToSIA03:RF-HeatSink-H03A:Tms-Mon | N/A | N/A | Memorias[0].8 | Digital | Input | N/A | N/A |  | Memorias[0].8 | .1
60 | Termostato da Barra Dissipadora 03B | RA | ToSIA03 | RF | HeatSink | H03B | Tms | Mon | RA-ToSIA03:RF-HeatSink-H03B:Tms-Mon | N/A | N/A | Memorias[0].9 | Digital | Input | N/A | N/A |  | Memorias[0].9 | .1
61 | Termostato da Barra Dissipadora 04A | RA | ToSIA03 | RF | HeatSink | H04A | Tms | Mon | RA-ToSIA03:RF-HeatSink-H04A:Tms-Mon | N/A | N/A | Memorias[0].10 | Digital | Input | N/A | N/A |  | Memorias[0].10 | .1
62 | Termostato da Barra Dissipadora 04B | RA | ToSIA03 | RF | HeatSink | H04B | Tms | Mon | RA-ToSIA03:RF-HeatSink-H04B:Tms-Mon | N/A | N/A | Memorias[0].11 | Digital | Input | N/A | N/A |  | Memorias[0].11 | .1
63 | Termostato da Barra Dissipadora 05A | RA | ToSIA03 | RF | HeatSink | H05A | Tms | Mon | RA-ToSIA03:RF-HeatSink-H05A:Tms-Mon | N/A | N/A | Memorias[0].12 | Digital | Input | N/A | N/A |  | Memorias[0].12 | .1
64 | Termostato da Barra Dissipadora 05B | RA | ToSIA03 | RF | HeatSink | H05B | Tms | Mon | RA-ToSIA03:RF-HeatSink-H05B:Tms-Mon | N/A | N/A | Memorias[0].13 | Digital | Input | N/A | N/A |  | Memorias[0].13 | .1
65 | Termostato da Barra Dissipadora 06A | RA | ToSIA03 | RF | HeatSink | H06A | Tms | Mon | RA-ToSIA03:RF-HeatSink-H06A:Tms-Mon | N/A | N/A | Memorias[0].14 | Digital | Input | N/A | N/A |  | Memorias[0].14 | .1
66 | Termostato da Barra Dissipadora 06B | RA | ToSIA03 | RF | HeatSink | H06B | Tms | Mon | RA-ToSIA03:RF-HeatSink-H06B:Tms-Mon | N/A | N/A | Memorias[0].15 | Digital | Input | N/A | N/A |  | Memorias[0].15 | .1
67 | Termostato da Barra Dissipadora 07A | RA | ToSIA03 | RF | HeatSink | H07A | Tms | Mon | RA-ToSIA03:RF-HeatSink-H07A:Tms-Mon | N/A | N/A | Memorias[0].16 | Digital | Input | N/A | N/A |  | Memorias[0].16 | .1
68 | Termostato da Barra Dissipadora 07B | RA | ToSIA03 | RF | HeatSink | H07B | Tms | Mon | RA-ToSIA03:RF-HeatSink-H07B:Tms-Mon | N/A | N/A | Memorias[0].17 | Digital | Input | N/A | N/A |  | Memorias[0].17 | .1
69 | Termostato da Barra Dissipadora 08A | RA | ToSIA03 | RF | HeatSink | H08A | Tms | Mon | RA-ToSIA03:RF-HeatSink-H08A:Tms-Mon | N/A | N/A | Memorias[0].18 | Digital | Input | N/A | N/A |  | Memorias[0].18 | .1
70 | Termostato da Barra Dissipadora 08B | RA | ToSIA03 | RF | HeatSink | H08B | Tms | Mon | RA-ToSIA03:RF-HeatSink-H08B:Tms-Mon | N/A | N/A | Memorias[0].19 | Digital | Input | N/A | N/A |  | Memorias[0].19 | .1
71 | Interlock Geral SSA 3 | RA | ToSIA03 | RF | SSAmpTower | - | Sts | Mon | RA-ToSIA03:RF-SSAmpTower:Sts-Mon | N/A | N/A | Memorias[2].8 | Digital | Input | N/A | N/A |  | Memorias[2].8 | .1
72 | Rotâmetro Torre 03 do Anel | RA | ToSIA03 | RF | SSAmpTower | - | HdFlwRt | Mon | RA-ToSIA03:RF-SSAmpTower:HdFlwRt-Mon | N/A | N/A | Memorias[1].20 | Digital | Input | N/A | N/A |  | Memorias[1].20 | .1
73 | 48V das Fontes TDK Torre 03 Off | RA | ToSIA03 | RF | TDKSource | - | PwrDCDsbl | Sel | RA-ToSIA03:RF-TDKSource:PwrDCDsbl-Sel | N/A | N/A | Memorias[2].30 | Digital | Control | N/A | N/A |  | Memorias[2].30 | .1 |  | 0.5
74 | 48V das Fontes TDK Torre 03 On | RA | ToSIA03 | RF | TDKSource | - | PwrDCEnbl | Sel | RA-ToSIA03:RF-TDKSource:PwrDCEnbl-Sel | N/A | N/A | Memorias[2].25 | Digital | Control | N/A | N/A |  | Memorias[2].25 | .1 |  | 0.5
75 | 48V das Fontes TDK Torre 03 Status | RA | ToSIA03 | RF | TDKSource | - | PwrDC | Sts | RA-ToSIA03:RF-TDKSource:PwrDC-Sts | N/A | N/A | Remote_01_Torre_Teste:8:O.Pt05.Data | Digital | Input | N/A | N/A |  | Remote_01_Torre_Teste:8:O.Pt05.Data | .1
76 | Falha Ac Mini Rack 1 Torre 03 | RA | ToSIA03 | RF | TDKSource | R1 | StsAC | Mon | RA-ToSIA03:RF-TDKSource-R1:StsAC-Mon | N/A | N/A | Memorias[2].18 | Digital | Input | N/A | N/A |  | Memorias[2].18 | .1
77 | Falha Ac Mini Rack 2 Torre 03 | RA | ToSIA03 | RF | TDKSource | R2 | StsAC | Mon | RA-ToSIA03:RF-TDKSource-R2:StsAC-Mon | N/A | N/A | Memorias[2].19 | Digital | Input | N/A | N/A |  | Memorias[2].19 | .1
78 | Falha Ac Mini Rack 3 Torre 3 | RA | ToSIA03 | RF | TDKSource | R3 | StsAC | Mon | RA-ToSIA03:RF-TDKSource-R3:StsAC-Mon | N/A | N/A | Memorias[2].20 | Digital | Input | N/A | N/A |  | Memorias[2].20 | .1
79 | Falha Ac Mini Rack 4 Torre 3 | RA | ToSIA03 | RF | TDKSource | R4 | StsAC | Mon | RA-ToSIA03:RF-TDKSource-R4:StsAC-Mon | N/A | N/A | Memorias[2].21 | Digital | Input | N/A | N/A |  | Memorias[2].21 | .1
80 | Interlock externo do CLP para Painel Torre 03 (Saída) | RA | ToSIA03 | RF | Intlk | - | IntlkACPanel | Mon | RA-ToSIA03:RF-Intlk:IntlkACPanel-Mon | N/A | N/A | Remote_01_Torre_Teste:8:O.Pt04.Data | Digital | Input | N/A | N/A |  | Remote_01_Torre_Teste:8:O.Pt04.Data | .1
81 | Torre 03 Enbl | RA | ToSIA03 | RF | SSAmpTower | - | Enbl | Sel | RA-ToSIA03:RF-SSAmpTower:Enbl-Sel | N/A | N/A | Memorias[19].16 | Digital | Control | N/A | N/A |  | Memorias[19].16 | .1
82 | Torre 03 Enbl Sts | RA | ToSIA03 | RF | SSAmpTower | - | Enbl | Sts | RA-ToSIA03:RF-SSAmpTower:Enbl-Sts | N/A | N/A | Memorias[19].17 | Digital | Input | N/A | N/A |  | Memorias[19].17 | .1
83 | Falha Fusível eletrônico | RA | ToSIA03 | RF | CtrlPanel | - | PwrSts | Mon | RA-ToSIA03:RF-CtrlPanel:PwrSts-Mon | N/A | N/A | Memorias[0].0 | Digital | Input | N/A | N/A |  | Memorias[0].0 | .1
84 | Falha fonte 24VDC | RA | ToSIA03 | RF | ACPanel | - | StsPos24V | Mon | RA-ToSIA03:RF-ACPanel:StsPos24V-Mon | N/A | N/A | Memorias[0].1 | Digital | Input | N/A | N/A |  | Memorias[0].1 | .1
85 | Medida Potencia incidente de entrada | RA | ToSIA03 | RF | SSAmpTower | - | PwrFwdIn | Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdIn-Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdInUpperLimit-Cte | N/A | Remote_01_Torre_Teste:5:I.Ch00.Data | Analog | Input | Real[4] | N/A |  | Remote_01_Torre_Teste:5:I.Ch00.Data | .1 | 2 |  | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0
86 | Medida Potencia Refletida de entrada | RA | ToSIA03 | RF | SSAmpTower | - | PwrRevIn | Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevIn-Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevInUpperLimit-Cte | N/A | Remote_01_Torre_Teste:5:I.Ch01.Data | Analog | Input | Real[5] | N/A |  | Remote_01_Torre_Teste:5:I.Ch01.Data | .1 | 2 |  | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0
87 | Medida Potencia incidente de saída | RA | ToSIA03 | RF | SSAmpTower | - | PwrFwdOut | Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdOut-Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdOutUpperLimit-Cte | N/A | Remote_01_Torre_Teste:5:I.Ch02.Data | Analog | Input | Real[6] | N/A |  | Remote_01_Torre_Teste:5:I.Ch02.Data | .1 | 2 |  | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0
88 | Medida Potencia refletida de saída | RA | ToSIA03 | RF | SSAmpTower | - | PwrRevOut | Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevOut-Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevOutUpperLimit-Cte | N/A | Remote_01_Torre_Teste:5:I.Ch03.Data | Analog | Input | Real[7] | N/A |  | Remote_01_Torre_Teste:5:I.Ch03.Data | .1 | 2 |  | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0 | 0*pv^4 + 0*pv^3 + 0*pv^2 + 1*pv + 0
89 | Falha Pot Incidente de entrada | RA | ToSIA03 | RF | SSAmpTower | - | PwrFwdInSts | Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdInSts-Mon | N/A | N/A | Falha_Pot_RF.0 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.0 | .1
90 | Falha Pot Refletida de entrada | RA | ToSIA03 | RF | SSAmpTower | - | PwrRevInSts | Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevInSts-Mon | N/A | N/A | Falha_Pot_RF.1 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.1 | .1
91 | Falha Pot Incidente de Saída | RA | ToSIA03 | RF | SSAmpTower | - | PwrFwdOutSts | Mon | RA-ToSIA03:RF-SSAmpTower:PwrFwdOutSts-Mon | N/A | N/A | Falha_Pot_RF.2 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.2 | .1
92 | Falha Pot Refletida de Saída | RA | ToSIA03 | RF | SSAmpTower | - | PwrRevOutSts | Mon | RA-ToSIA03:RF-SSAmpTower:PwrRevOutSts-Mon | N/A | N/A | Falha_Pot_RF.3 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.3 | .1
93 | Falha Pot RF torre 03 | RA | ToSIA03 | RF | SSAmpTower | - | RFPwrSts | Mon | RA-ToSIA03:RF-SSAmpTower:RFPwrSts-Mon | N/A | N/A | Falha_Pot_RF.4 | Digital | Input | N/A | N/A |  | Falha_Pot_RF.4 | .1
94 | Hablita coaxial switch torre 03 | RA | ToSIA03 | RF | CtrlPanel | - | PINSwEnbl | Cmd | RA-ToSIA03:RF-CtrlPanel:PINSwEnbl-Cmd | N/A | N/A | Memorias[3].16 | Digital | Control | N/A | N/A |  | Memorias[3].16 | .1 |  | 0.5
95 | Desabilita coaxial switch torre 03 | RA | ToSIA03 | RF | CtrlPanel | - | PINSwDsbl | Cmd | RA-ToSIA03:RF-CtrlPanel:PINSwDsbl-Cmd | N/A | N/A | Memorias[3].18 | Digital | Control | N/A | N/A |  | Memorias[3].18 | .1 |  | 0.5
96 | Status coaxial switch torre 03 | RA | ToSIA03 | RF | CtrlPanel | - | PINSwSts | Mon | RA-ToSIA03:RF-CtrlPanel:PINSwSts-Mon | N/A | N/A | Remote_01_Torre_Teste:8:O.Pt06.Data | Digital | Output | N/A | N/A |  | Remote_01_Torre_Teste:8:O.Pt06.Data | .1
97 | Horímetro Torre 03 | RA | ToSIA03 | RF | SSAmpTower | - | RunHour | Mon | RA-ToSIA03:RF-SSAmpTower:RunHour-Mon | N/A | N/A | Real[10] | Analog | Input | N/A | N/A | h | Real[10] | .1
98 | Falha Rotâmetro Carga 80kw | RA | ToSIA03 | RF | WaterLoad | - | HdFlwRt | Mon | RA-ToSIA03:RF-WaterLoad:HdFlwRt-Mon | N/A | N/A | Memorias[1].20 | Digital | Input | N/A | N/A |  | Memorias[1].20 | .1

## SSAmp Tower 03 Multi ABB
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Corrente de Fase 1 | RA | ToSIA03 | RF | ACPanel | - | PhsCurrent1 | Mon | RA-ToSIA03:RF-ACPanel:PhsCurrent1-Mon | N/A | N/A | RA_ToSIA03_RF_ACPanel_PhsCurrent1Mon | Digital | Input | N/A | N/A |  | RA_ToSIA03_RF_ACPanel_PhsCurrent1Mon | .1
2 | Corrente de Fase 2 | RA | ToSIA03 | RF | ACPanel | - | PhsCurrent2 | Mon | RA-ToSIA03:RF-ACPanel:PhsCurrent2-Mon | N/A | N/A | RA_ToSIA03_RF_ACPanel_PhsCurrent2Mon | Digital | Input | N/A | N/A |  | RA_ToSIA03_RF_ACPanel_PhsCurrent2Mon | .1
3 | Corrente de Fase 3 | RA | ToSIA03 | RF | ACPanel | - | PhsCurrent3 | Mon | RA-ToSIA03:RF-ACPanel:PhsCurrent3-Mon | RA-ToSIA03:RF-ACPanel:PhsCurrent3UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:PhsCurrent3LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_PhsCurrent3Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_PhsCurrent3Mon | .5 | 2
4 | Tensão Fase 1 | RA | ToSIA03 | RF | ACPanel | - | PhsVoltage1 | Mon | RA-ToSIA03:RF-ACPanel:PhsVoltage1-Mon | RA-ToSIA03:RF-ACPanel:PhsVoltage1UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:PhsVoltage1LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_PhsVoltage1Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_PhsVoltage1Mon | .5 | 2
5 | Tensão Fase 2 | RA | ToSIA03 | RF | ACPanel | - | PhsVoltage2 | Mon | RA-ToSIA03:RF-ACPanel:PhsVoltage2-Mon | RA-ToSIA03:RF-ACPanel:PhsVoltage2UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:PhsVoltage2LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_PhsVoltage2Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_PhsVoltage2Mon | .5 | 2
6 | Tensão Fase 3 | RA | ToSIA03 | RF | ACPanel | - | PhsVoltage3 | Mon | RA-ToSIA03:RF-ACPanel:PhsVoltage3-Mon | RA-ToSIA03:RF-ACPanel:PhsVoltage3UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:PhsVoltage3LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_PhsVoltage3Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_PhsVoltage3Mon | .5 | 2
7 | Tensão de linha 12 | RA | ToSIA03 | RF | ACPanel | - | LineVoltage12 | Mon | RA-ToSIA03:RF-ACPanel:LineVoltage12-Mon | RA-ToSIA03:RF-ACPanel:LineVoltage12UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:LineVoltage12LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_LineVoltage12Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_LineVoltage12Mon | .5 | 2
8 | Tensão de linha 13 | RA | ToSIA03 | RF | ACPanel | - | LineVoltage13 | Mon | RA-ToSIA03:RF-ACPanel:LineVoltage13-Mon | RA-ToSIA03:RF-ACPanel:LineVoltage13UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:LineVoltage13LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_LineVoltage13Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_LineVoltage13Mon | .5 | 2
9 | Tensão de linha 23 | RA | ToSIA03 | RF | ACPanel | - | LineVoltage23 | Mon | RA-ToSIA03:RF-ACPanel:LineVoltage23-Mon | RA-ToSIA03:RF-ACPanel:LineVoltage23UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:LineVoltage23LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_LineVoltage23Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_LineVoltage23Mon | .5 | 2
10 | Potência S | RA | ToSIA03 | RF | ACPanel | - | PwrS | Mon | RA-ToSIA03:RF-ACPanel:PwrS-Mon | RA-ToSIA03:RF-ACPanel:PwrSUpperLimit-Cte | RA-ToSIA03:RF-ACPanel:PwrSLowerLimit-Cte | RA_ToSIA03_RF_ACPanel_PwrSMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_PwrSMon | .5 | 2
11 | Potencia P | RA | ToSIA03 | RF | ACPanel | - | PwrP | Mon | RA-ToSIA03:RF-ACPanel:PwrP-Mon | RA-ToSIA03:RF-ACPanel:PwrPUpperLimit-Cte | RA-ToSIA03:RF-ACPanel:PwrPLowerLimit-Cte | RA_ToSIA03_RF_ACPanel_PwrPMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_PwrPMon | .5 | 2
12 | Potência Q | RA | ToSIA03 | RF | ACPanel | - | PwrQ | Mon | RA-ToSIA03:RF-ACPanel:PwrQ-Mon | RA-ToSIA03:RF-ACPanel:PwrQUpperLimit-Cte | RA-ToSIA03:RF-ACPanel:PwrQLowerLimit-Cte | RA_ToSIA03_RF_ACPanel_PwrQMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_PwrQMon | .5 | 2
13 | Fator de potência | RA | ToSIA03 | RF | ACPanel | - | PwrFactor | Mon | RA-ToSIA03:RF-ACPanel:PwrFactor-Mon | RA-ToSIA03:RF-ACPanel:PwrFactorUpperLimit-Cte | RA-ToSIA03:RF-ACPanel:PwrFactorLowerLimit-Cte | RA_ToSIA03_RF_ACPanel_PwrFactorMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_PwrFactorMon | .5 | 2
14 | THD 1 | RA | ToSIA03 | RF | ACPanel | - | THD1 | Mon | RA-ToSIA03:RF-ACPanel:THD1-Mon | RA-ToSIA03:RF-ACPanel:THD1UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:THD1LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_THD1Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_THD1Mon | .5 | 2
15 | THD 2 | RA | ToSIA03 | RF | ACPanel | - | THD2 | Mon | RA-ToSIA03:RF-ACPanel:THD2-Mon | RA-ToSIA03:RF-ACPanel:THD2UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:THD2LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_THD2Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_THD2Mon | .5 | 2
16 | THD 3 | RA | ToSIA03 | RF | ACPanel | - | THD3 | Mon | RA-ToSIA03:RF-ACPanel:THD3-Mon | RA-ToSIA03:RF-ACPanel:THD3UpperLimit-Cte | RA-ToSIA03:RF-ACPanel:THD3LowerLimit-Cte | RA_ToSIA03_RF_ACPanel_THD3Mon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_THD3Mon | .5 | 2
17 | Corrente Neutro | RA | ToSIA03 | RF | ACPanel | - | CurrentN | Mon | RA-ToSIA03:RF-ACPanel:CurrentN-Mon | RA-ToSIA03:RF-ACPanel:CurrentNUpperLimit-Cte | RA-ToSIA03:RF-ACPanel:CurrentNLowerLimit-Cte | RA_ToSIA03_RF_ACPanel_CurrentNMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_CurrentNMon | .5 | 2
18 | Frequencia | RA | ToSIA03 | RF | ACPanel | - | Freq | Mon | RA-ToSIA03:RF-ACPanel:Freq-Mon | RA-ToSIA03:RF-ACPanel:FreqUpperLimit-Cte | RA-ToSIA03:RF-ACPanel:FreqLowerLimit-Cte | RA_ToSIA03_RF_ACPanel_FreqMon | Analog | Input | Real[0] | Real[1] | C | RA_ToSIA03_RF_ACPanel_FreqMon | .5 | 2

## SSAmp Tower 02
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | AC da Torre 02 do Anel Status | RA | ToSIA02 | RF | ACPanel | - | PwrACOp | Mon | RA-ToSIA02:RF-ACPanel:PwrACOp-Mon | N/A | N/A | RA_ToSIA02_RF_ACPanel_PwrACOpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_ACPanel_PwrACOpMon | .1
2 | AC das Fontes TDK Torre 02 Off | RA | ToSIA02 | RF | ACPanel | - | PwrACDsbl | Sel | RA-ToSIA02:RF-ACPanel:PwrACDsbl-Sel | N/A | N/A | RA_ToSIA02_RF_ACPanel_PwrACDsblSel | Digital | Control |  |  |  | RA_ToSIA02_RF_ACPanel_PwrACDsblSel | .1
3 | AC das Fontes TDK Torre 02 On | RA | ToSIA02 | RF | ACPanel | - | PwrACEnbl | Sel | RA-ToSIA02:RF-ACPanel:PwrACEnbl-Sel | N/A | N/A | RA_ToSIA02_RF_ACPanel_PwrACEnblSel | Digital | Control |  |  |  | RA_ToSIA02_RF_ACPanel_PwrACEnblSel | .1
4 | AC das Fontes TDK Torre 02 Status | RA | ToSIA02 | RF | ACPanel | - | PwrAC | Sts | RA-ToSIA02:RF-ACPanel:PwrAC-Sts | N/A | N/A | RA_ToSIA02_RF_ACPanel_PwrACSts | Digital | Output |  |  |  | RA_ToSIA02_RF_ACPanel_PwrACSts | .1
5 | Falta de Fase do Painel Torre 02 do Anel | RA | ToSIA02 | RF | ACPanel | - | PhsFlt | Mon | RA-ToSIA02:RF-ACPanel:PhsFlt-Mon | N/A | N/A | RA_ToSIA02_RF_ACPanel_PhsFltMon | Digital | Input |  |  |  | RA_ToSIA02_RF_ACPanel_PhsFltMon | .1
6 | Interlock externo do Painel Torre 02 | RA | ToSIA02 | RF | ACPanel | - | Intlk | Mon | RA-ToSIA02:RF-ACPanel:Intlk-Mon | N/A | N/A | RA_ToSIA02_RF_ACPanel_IntlkMon | Digital | Input |  |  |  | RA_ToSIA02_RF_ACPanel_IntlkMon | .1
7 | PT-100 da Barra Dissipadora 01A | RA | ToSIA02 | RF | HeatSink | H01A | T | Mon | RA-ToSIA02:RF-HeatSink-H01A:T-Mon | RA-ToSIA02:RF-HeatSink-H01A:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H01A:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H01A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H01A_TMon | .5 | 2
8 | PT-100 da Barra Dissipadora 01B | RA | ToSIA02 | RF | HeatSink | H01B | T | Mon | RA-ToSIA02:RF-HeatSink-H01B:T-Mon | RA-ToSIA02:RF-HeatSink-H01B:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H01B:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H01B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H01B_TMon | .5 | 2
9 | PT-100 da Barra Dissipadora 02A | RA | ToSIA02 | RF | HeatSink | H02A | T | Mon | RA-ToSIA02:RF-HeatSink-H02A:T-Mon | RA-ToSIA02:RF-HeatSink-H02A:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H02A:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H02A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H02A_TMon | .5 | 2
10 | PT-100 da Barra Dissipadora 02B | RA | ToSIA02 | RF | HeatSink | H02B | T | Mon | RA-ToSIA02:RF-HeatSink-H02B:T-Mon | RA-ToSIA02:RF-HeatSink-H02B:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H02B:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H02B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H02B_TMon | .5 | 2
11 | PT-100 da Barra Dissipadora 03A | RA | ToSIA02 | RF | HeatSink | H03A | T | Mon | RA-ToSIA02:RF-HeatSink-H03A:T-Mon | RA-ToSIA02:RF-HeatSink-H03A:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H03A:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H03A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H03A_TMon | .5 | 2
12 | PT-100 da Barra Dissipadora 03B | RA | ToSIA02 | RF | HeatSink | H03B | T | Mon | RA-ToSIA02:RF-HeatSink-H03B:T-Mon | RA-ToSIA02:RF-HeatSink-H03B:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H03B:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H03B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H03B_TMon | .5 | 2
13 | PT-100 da Barra Dissipadora 04A | RA | ToSIA02 | RF | HeatSink | H04A | T | Mon | RA-ToSIA02:RF-HeatSink-H04A:T-Mon | RA-ToSIA02:RF-HeatSink-H04A:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H04A:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H04A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H04A_TMon | .5 | 2
14 | PT-100 da Barra Dissipadora 04B | RA | ToSIA02 | RF | HeatSink | H04B | T | Mon | RA-ToSIA02:RF-HeatSink-H04B:T-Mon | RA-ToSIA02:RF-HeatSink-H04B:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H04B:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H04B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H04B_TMon | .5 | 2
15 | PT-100 da Barra Dissipadora 05A | RA | ToSIA02 | RF | HeatSink | H05A | T | Mon | RA-ToSIA02:RF-HeatSink-H05A:T-Mon | RA-ToSIA02:RF-HeatSink-H05A:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H05A:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H05A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H05A_TMon | .5 | 2
16 | PT-100 da Barra Dissipadora 05B | RA | ToSIA02 | RF | HeatSink | H05B | T | Mon | RA-ToSIA02:RF-HeatSink-H05B:T-Mon | RA-ToSIA02:RF-HeatSink-H05B:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H05B:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H05B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H05B_TMon | .5 | 2
17 | PT-100 da Barra Dissipadora 06A | RA | ToSIA02 | RF | HeatSink | H06A | T | Mon | RA-ToSIA02:RF-HeatSink-H06A:T-Mon | RA-ToSIA02:RF-HeatSink-H06A:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H06A:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H06A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H06A_TMon | .5 | 2
18 | PT-100 da Barra Dissipadora 06B | RA | ToSIA02 | RF | HeatSink | H06B | T | Mon | RA-ToSIA02:RF-HeatSink-H06B:T-Mon | RA-ToSIA02:RF-HeatSink-H06B:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H06B:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H06B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H06B_TMon | .5 | 2
19 | PT-100 da Barra Dissipadora 07A | RA | ToSIA02 | RF | HeatSink | H07A | T | Mon | RA-ToSIA02:RF-HeatSink-H07A:T-Mon | RA-ToSIA02:RF-HeatSink-H07A:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H07A:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H07A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H07A_TMon | .5 | 2
20 | PT-100 da Barra Dissipadora 07B | RA | ToSIA02 | RF | HeatSink | H07B | T | Mon | RA-ToSIA02:RF-HeatSink-H07B:T-Mon | RA-ToSIA02:RF-HeatSink-H07B:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H07B:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H07B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H07B_TMon | .5 | 2
21 | PT-100 da Barra Dissipadora 08A | RA | ToSIA02 | RF | HeatSink | H08A | T | Mon | RA-ToSIA02:RF-HeatSink-H08A:T-Mon | RA-ToSIA02:RF-HeatSink-H08A:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H08A:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H08A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H08A_TMon | .5 | 2
22 | PT-100 da Barra Dissipadora 08B | RA | ToSIA02 | RF | HeatSink | H08B | T | Mon | RA-ToSIA02:RF-HeatSink-H08B:T-Mon | RA-ToSIA02:RF-HeatSink-H08B:TUpperLimit-Cte | RA-ToSIA02:RF-HeatSink-H08B:TLowerLimit-Cte | RA_ToSIA02_RF_HeatSink_H08B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA02_RF_HeatSink_H08B_TMon | .5 | 2
23 | Temperatura abaixo do set da Barra Dissipadora 01A | RA | ToSIA02 | RF | HeatSink | H01A | TDown | Mon | RA-ToSIA02:RF-HeatSink-H01A:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H01A_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H01A_TDownMon | .1
24 | Temperatura abaixo do set da Barra Dissipadora 01B | RA | ToSIA02 | RF | HeatSink | H01B | TDown | Mon | RA-ToSIA02:RF-HeatSink-H01B:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H01B_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H01B_TDownMon | .1
25 | Temperatura abaixo do set da Barra Dissipadora 02A | RA | ToSIA02 | RF | HeatSink | H02A | TDown | Mon | RA-ToSIA02:RF-HeatSink-H02A:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H02A_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H02A_TDownMon | .1
26 | Temperatura abaixo do set da Barra Dissipadora 02B | RA | ToSIA02 | RF | HeatSink | H02B | TDown | Mon | RA-ToSIA02:RF-HeatSink-H02B:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H02B_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H02B_TDownMon | .1
27 | Temperatura abaixo do set da Barra Dissipadora 03A | RA | ToSIA02 | RF | HeatSink | H03A | TDown | Mon | RA-ToSIA02:RF-HeatSink-H03A:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H03A_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H03A_TDownMon | .1
28 | Temperatura abaixo do set da Barra Dissipadora 03B | RA | ToSIA02 | RF | HeatSink | H03B | TDown | Mon | RA-ToSIA02:RF-HeatSink-H03B:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H03B_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H03B_TDownMon | .1
29 | Temperatura abaixo do set da Barra Dissipadora 04A | RA | ToSIA02 | RF | HeatSink | H04A | TDown | Mon | RA-ToSIA02:RF-HeatSink-H04A:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H04A_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H04A_TDownMon | .1
30 | Temperatura abaixo do set da Barra Dissipadora 04B | RA | ToSIA02 | RF | HeatSink | H04B | TDown | Mon | RA-ToSIA02:RF-HeatSink-H04B:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H04B_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H04B_TDownMon | .1
31 | Temperatura abaixo do set da Barra Dissipadora 05A | RA | ToSIA02 | RF | HeatSink | H05A | TDown | Mon | RA-ToSIA02:RF-HeatSink-H05A:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H05A_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H05A_TDownMon | .1
32 | Temperatura abaixo do set da Barra Dissipadora 05B | RA | ToSIA02 | RF | HeatSink | H05B | TDown | Mon | RA-ToSIA02:RF-HeatSink-H05B:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H05B_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H05B_TDownMon | .1
33 | Temperatura abaixo do set da Barra Dissipadora 06A | RA | ToSIA02 | RF | HeatSink | H06A | TDown | Mon | RA-ToSIA02:RF-HeatSink-H06A:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H06A_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H06A_TDownMon | .1
34 | Temperatura abaixo do set da Barra Dissipadora 06B | RA | ToSIA02 | RF | HeatSink | H06B | TDown | Mon | RA-ToSIA02:RF-HeatSink-H06B:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H06B_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H06B_TDownMon | .1
35 | Temperatura abaixo do set da Barra Dissipadora 07A | RA | ToSIA02 | RF | HeatSink | H07A | TDown | Mon | RA-ToSIA02:RF-HeatSink-H07A:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H07A_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H07A_TDownMon | .1
36 | Temperatura abaixo do set da Barra Dissipadora 07B | RA | ToSIA02 | RF | HeatSink | H07B | TDown | Mon | RA-ToSIA02:RF-HeatSink-H07B:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H07B_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H07B_TDownMon | .1
37 | Temperatura abaixo do set da Barra Dissipadora 08A | RA | ToSIA02 | RF | HeatSink | H08A | TDown | Mon | RA-ToSIA02:RF-HeatSink-H08A:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H08A_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H08A_TDownMon | .1
38 | Temperatura abaixo do set da Barra Dissipadora 08B | RA | ToSIA02 | RF | HeatSink | H08B | TDown | Mon | RA-ToSIA02:RF-HeatSink-H08B:TDown-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H08B_TDownMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H08B_TDownMon | .1
39 | Temperatura acima do set da Barra Dissipadora 01A | RA | ToSIA02 | RF | HeatSink | H01A | TUp | Mon | RA-ToSIA02:RF-HeatSink-H01A:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H01A_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H01A_TUpMon | .1
40 | Temperatura acima do set da Barra Dissipadora 01B | RA | ToSIA02 | RF | HeatSink | H01B | TUp | Mon | RA-ToSIA02:RF-HeatSink-H01B:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H01B_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H01B_TUpMon | .1
41 | Temperatura acima do set da Barra Dissipadora 02A | RA | ToSIA02 | RF | HeatSink | H02A | TUp | Mon | RA-ToSIA02:RF-HeatSink-H02A:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H02A_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H02A_TUpMon | .1
42 | Temperatura acima do set da Barra Dissipadora 02B | RA | ToSIA02 | RF | HeatSink | H02B | TUp | Mon | RA-ToSIA02:RF-HeatSink-H02B:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H02B_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H02B_TUpMon | .1
43 | Temperatura acima do set da Barra Dissipadora 03A | RA | ToSIA02 | RF | HeatSink | H03A | TUp | Mon | RA-ToSIA02:RF-HeatSink-H03A:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H03A_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H03A_TUpMon | .1
44 | Temperatura acima do set da Barra Dissipadora 03B | RA | ToSIA02 | RF | HeatSink | H03B | TUp | Mon | RA-ToSIA02:RF-HeatSink-H03B:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H03B_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H03B_TUpMon | .1
45 | Temperatura acima do set da Barra Dissipadora 04A | RA | ToSIA02 | RF | HeatSink | H04A | TUp | Mon | RA-ToSIA02:RF-HeatSink-H04A:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H04A_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H04A_TUpMon | .1
46 | Temperatura acima do set da Barra Dissipadora 04B | RA | ToSIA02 | RF | HeatSink | H04B | TUp | Mon | RA-ToSIA02:RF-HeatSink-H04B:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H04B_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H04B_TUpMon | .1
47 | Temperatura acima do set da Barra Dissipadora 05A | RA | ToSIA02 | RF | HeatSink | H05A | TUp | Mon | RA-ToSIA02:RF-HeatSink-H05A:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H05A_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H05A_TUpMon | .1
48 | Temperatura acima do set da Barra Dissipadora 05B | RA | ToSIA02 | RF | HeatSink | H05B | TUp | Mon | RA-ToSIA02:RF-HeatSink-H05B:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H05B_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H05B_TUpMon | .1
49 | Temperatura acima do set da Barra Dissipadora 06A | RA | ToSIA02 | RF | HeatSink | H06A | TUp | Mon | RA-ToSIA02:RF-HeatSink-H06A:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H06A_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H06A_TUpMon | .1
50 | Temperatura acima do set da Barra Dissipadora 06B | RA | ToSIA02 | RF | HeatSink | H06B | TUp | Mon | RA-ToSIA02:RF-HeatSink-H06B:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H06B_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H06B_TUpMon | .1
51 | Temperatura acima do set da Barra Dissipadora 07A | RA | ToSIA02 | RF | HeatSink | H07A | TUp | Mon | RA-ToSIA02:RF-HeatSink-H07A:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H07A_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H07A_TUpMon | .1
52 | Temperatura acima do set da Barra Dissipadora 07B | RA | ToSIA02 | RF | HeatSink | H07B | TUp | Mon | RA-ToSIA02:RF-HeatSink-H07B:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H07B_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H07B_TUpMon | .1
53 | Temperatura acima do set da Barra Dissipadora 08A | RA | ToSIA02 | RF | HeatSink | H08A | TUp | Mon | RA-ToSIA02:RF-HeatSink-H08A:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H08A_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H08A_TUpMon | .1
54 | Temperatura acima do set da Barra Dissipadora 08B | RA | ToSIA02 | RF | HeatSink | H08B | TUp | Mon | RA-ToSIA02:RF-HeatSink-H08B:TUp-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H08B_TUpMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H08B_TUpMon | .1
55 | Termostato da Barra Dissipadora 01A | RA | ToSIA02 | RF | HeatSink | H01A | Tms | Mon | RA-ToSIA02:RF-HeatSink-H01A:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H01A_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H01A_TmsMon | .1
56 | Termostato da Barra Dissipadora 01B | RA | ToSIA02 | RF | HeatSink | H01B | Tms | Mon | RA-ToSIA02:RF-HeatSink-H01B:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H01B_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H01B_TmsMon | .1
57 | Termostato da Barra Dissipadora 02A | RA | ToSIA02 | RF | HeatSink | H02A | Tms | Mon | RA-ToSIA02:RF-HeatSink-H02A:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H02A_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H02A_TmsMon | .1
58 | Termostato da Barra Dissipadora 02B | RA | ToSIA02 | RF | HeatSink | H02B | Tms | Mon | RA-ToSIA02:RF-HeatSink-H02B:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H02B_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H02B_TmsMon | .1
59 | Termostato da Barra Dissipadora 03A | RA | ToSIA02 | RF | HeatSink | H03A | Tms | Mon | RA-ToSIA02:RF-HeatSink-H03A:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H03A_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H03A_TmsMon | .1
60 | Termostato da Barra Dissipadora 03B | RA | ToSIA02 | RF | HeatSink | H03B | Tms | Mon | RA-ToSIA02:RF-HeatSink-H03B:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H03B_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H03B_TmsMon | .1
61 | Termostato da Barra Dissipadora 04A | RA | ToSIA02 | RF | HeatSink | H04A | Tms | Mon | RA-ToSIA02:RF-HeatSink-H04A:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H04A_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H04A_TmsMon | .1
62 | Termostato da Barra Dissipadora 04B | RA | ToSIA02 | RF | HeatSink | H04B | Tms | Mon | RA-ToSIA02:RF-HeatSink-H04B:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H04B_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H04B_TmsMon | .1
63 | Termostato da Barra Dissipadora 05A | RA | ToSIA02 | RF | HeatSink | H05A | Tms | Mon | RA-ToSIA02:RF-HeatSink-H05A:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H05A_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H05A_TmsMon | .1
64 | Termostato da Barra Dissipadora 05B | RA | ToSIA02 | RF | HeatSink | H05B | Tms | Mon | RA-ToSIA02:RF-HeatSink-H05B:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H05B_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H05B_TmsMon | .1
65 | Termostato da Barra Dissipadora 06A | RA | ToSIA02 | RF | HeatSink | H06A | Tms | Mon | RA-ToSIA02:RF-HeatSink-H06A:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H06A_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H06A_TmsMon | .1
66 | Termostato da Barra Dissipadora 06B | RA | ToSIA02 | RF | HeatSink | H06B | Tms | Mon | RA-ToSIA02:RF-HeatSink-H06B:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H06B_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H06B_TmsMon | .1
67 | Termostato da Barra Dissipadora 07A | RA | ToSIA02 | RF | HeatSink | H07A | Tms | Mon | RA-ToSIA02:RF-HeatSink-H07A:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H07A_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H07A_TmsMon | .1
68 | Termostato da Barra Dissipadora 07B | RA | ToSIA02 | RF | HeatSink | H07B | Tms | Mon | RA-ToSIA02:RF-HeatSink-H07B:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H07B_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H07B_TmsMon | .1
69 | Termostato da Barra Dissipadora 08A | RA | ToSIA02 | RF | HeatSink | H08A | Tms | Mon | RA-ToSIA02:RF-HeatSink-H08A:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H08A_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H08A_TmsMon | .1
70 | Termostato da Barra Dissipadora 08B | RA | ToSIA02 | RF | HeatSink | H08B | Tms | Mon | RA-ToSIA02:RF-HeatSink-H08B:Tms-Mon | N/A | N/A | RA_ToSIA02_RF_HeatSink_H08B_TmsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_HeatSink_H08B_TmsMon | .1
71 | Interlock Geral SSA 2 | RA | ToSIA02 | RF | SSAmpTower | - | Sts | Mon | RA-ToSIA02:RF-SSAmpTower:Sts-Mon | N/A | N/A | RA_ToSIA02_RF_SSAmpTower_StsMon | Digital | Input |  |  |  | RA_ToSIA02_RF_SSAmpTower_StsMon | .1
72 | Rotâmetro Torre 02 do Anel | RA | ToSIA02 | RF | SSAmpTower | - | HdFlwRt | Mon | RA-ToSIA02:RF-SSAmpTower:HdFlwRt-Mon | N/A | N/A | RA_ToSIA02_RF_SSAmpTower_HdFlwRtMon | Digital | Input |  |  |  | RA_ToSIA02_RF_SSAmpTower_HdFlwRtMon | .1
73 | 48V das Fontes TDK Torre 02 Off | RA | ToSIA02 | RF | TDKSource | - | PwrDCDsbl | Sel | RA-ToSIA02:RF-TDKSource:PwrDCDsbl-Sel | N/A | N/A | RA_ToSIA02_RF_TDKSource_PwrDCDsblSel | Digital | Control |  |  |  | RA_ToSIA02_RF_TDKSource_PwrDCDsblSel | .1
74 | 48V das Fontes TDK Torre 02 On | RA | ToSIA02 | RF | TDKSource | - | PwrDCEnbl | Sel | RA-ToSIA02:RF-TDKSource:PwrDCEnbl-Sel | N/A | N/A | RA_ToSIA02_RF_TDKSource_PwrDCEnblSel | Digital | Control |  |  |  | RA_ToSIA02_RF_TDKSource_PwrDCEnblSel | .1
75 | 48V das Fontes TDK Torre 02 Status | RA | ToSIA02 | RF | TDKSource | - | PwrDC | Sts | RA-ToSIA02:RF-TDKSource:PwrDC-Sts | N/A | N/A | RA_ToSIA02_RF_TDKSource_PwrDCSts | Digital | Input |  |  |  | RA_ToSIA02_RF_TDKSource_PwrDCSts | .1
76 | Falha Ac Mini Rack 1 Torre 2 | RA | ToSIA02 | RF | TDKSource | R1 | StsAC | Mon | RA-ToSIA02:RF-TDKSource-R1:StsAC-Mon | N/A | N/A | RA_ToSIA02_RF_TDKSource_R1_StsACMon | Digital | Input |  |  |  | RA_ToSIA02_RF_TDKSource_R1_StsACMon | .1
77 | Falha Ac Mini Rack 2 Torre 2 | RA | ToSIA02 | RF | TDKSource | R2 | StsAC | Mon | RA-ToSIA02:RF-TDKSource-R2:StsAC-Mon | N/A | N/A | RA_ToSIA02_RF_TDKSource_R2_StsACMon | Digital | Input |  |  |  | RA_ToSIA02_RF_TDKSource_R2_StsACMon | .1
78 | Falha Ac Mini Rack 3 Torre 2 | RA | ToSIA02 | RF | TDKSource | R3 | StsAC | Mon | RA-ToSIA02:RF-TDKSource-R3:StsAC-Mon | N/A | N/A | RA_ToSIA02_RF_TDKSource_R3_StsACMon | Digital | Input |  |  |  | RA_ToSIA02_RF_TDKSource_R3_StsACMon | .1
79 | Falha Ac Mini Rack 4 Torre 2 | RA | ToSIA02 | RF | TDKSource | R4 | StsAC | Mon | RA-ToSIA02:RF-TDKSource-R4:StsAC-Mon | N/A | N/A | RA_ToSIA02_RF_TDKSource_R4_StsACMon | Digital | Input |  |  |  | RA_ToSIA02_RF_TDKSource_R4_StsACMon | .1
80 | Interlock externo do CLP para Painel Torre 02 (Saída) | SI | 02SB | RF | Intlk | - | IntlkACPanel02 | Mon | SI-02SB:RF-Intlk:IntlkACPanel02-Mon | N/A | N/A | SI_02SB_RF_Intlk_IntlkACPanel02Mon | Digital | Input |  |  |  | SI_02SB_RF_Intlk_IntlkACPanel02Mon | .1
81 | Torre 2 Enbl | RA | ToSIA02 | RF | SSAmpTower | - | Enbl | Sel | RA-ToSIA02:RF-SSAmpTower:Enbl-Sel | N/A | N/A | RA_ToSIA02_RF_SSAmpTower_EnblSel | Digital | Control |  |  |  | RA_ToSIA02_RF_SSAmpTower_EnblSel | .1
82 | Torre 2 Enbl Sts | RA | ToSIA02 | RF | SSAmpTower | - | Enbl | Sts | RA-ToSIA02:RF-SSAmpTower:Enbl-Sts | N/A | N/A | RA_ToSIA02_RF_SSAmpTower_EnblSts | Digital | Input |  |  |  | RA_ToSIA02_RF_SSAmpTower_EnblSts | .1
83 | Temperatura Minirack 01 | RA | ToSIA02 | RF | SSAMux | 1 | T | Mon | RA-ToSIA02:RF-SSAMux-1:T-Mon | N/A | N/A | RA_ToSIA02_RF_Mux_1_TMon | Analog | Input |  |  | C | RA_ToSIA02_RF_Mux_1_TMon | .5 | 2
84 | Temperatura Minirack 02 | RA | ToSIA02 | RF | SSAMux | 2 | T | Mon | RA-ToSIA02:RF-SSAMux-2:T-Mon | N/A | N/A | RA_ToSIA02_RF_Mux_2_TMon | Analog | Input |  |  | C | RA_ToSIA02_RF_Mux_2_TMon | .5 | 2
85 | Temperatura Minirack 03 | RA | ToSIA02 | RF | SSAMux | 3 | T | Mon | RA-ToSIA02:RF-SSAMux-3:T-Mon | N/A | N/A | RA_ToSIA02_RF_Mux_3_TMon | Analog | Input |  |  | C | RA_ToSIA02_RF_Mux_3_TMon | .5 | 2
86 | Temperatura Minirack 04 | RA | ToSIA02 | RF | SSAMux | 4 | T | Mon | RA-ToSIA02:RF-SSAMux-4:T-Mon | N/A | N/A | RA_ToSIA02_RF_Mux_4_TMon | Analog | Input |  |  | C | RA_ToSIA02_RF_Mux_4_TMon | .5 | 2
87 | Corrente de Fase 1 | RA | ToSIA02 | RF | ACPanel | - | PhsCurrent1 | Mon | RA-ToSIA02:RF-ACPanel:PhsCurrent1-Mon | N/A | N/A
88 | Corrente de Fase 2 | RA | ToSIA02 | RF | ACPanel | - | PhsCurrent2 | Mon | RA-ToSIA02:RF-ACPanel:PhsCurrent2-Mon | N/A | N/A
89 | Corrente de Fase 3 | RA | ToSIA02 | RF | ACPanel | - | PhsCurrent3 | Mon | RA-ToSIA02:RF-ACPanel:PhsCurrent3-Mon | N/A | N/A
90 | Tensão Fase 1 | RA | ToSIA02 | RF | ACPanel | - | PhsVoltage1 | Mon | RA-ToSIA02:RF-ACPanel:PhsVoltage1-Mon | N/A | N/A
91 | Tensão Fase 2 | RA | ToSIA02 | RF | ACPanel | - | PhsVoltage2 | Mon | RA-ToSIA02:RF-ACPanel:PhsVoltage2-Mon | N/A | N/A
92 | Tensão Fase 3 | RA | ToSIA02 | RF | ACPanel | - | PhsVoltage3 | Mon | RA-ToSIA02:RF-ACPanel:PhsVoltage3-Mon | N/A | N/A
93 | Tensão de linha 12 | RA | ToSIA02 | RF | ACPanel | - | LineVoltage12 | Mon | RA-ToSIA02:RF-ACPanel:LineVoltage12-Mon | N/A | N/A
94 | Tensão de linha 13 | RA | ToSIA02 | RF | ACPanel | - | LineVoltage13 | Mon | RA-ToSIA02:RF-ACPanel:LineVoltage13-Mon | N/A | N/A
95 | Tensão de linha 23 | RA | ToSIA02 | RF | ACPanel | - | LineVoltage23 | Mon | RA-ToSIA02:RF-ACPanel:LineVoltage23-Mon | N/A | N/A
96 | Potência S | RA | ToSIA02 | RF | ACPanel | - | PwrS | Mon | RA-ToSIA02:RF-ACPanel:PwrS-Mon | N/A | N/A
97 | Potencia P | RA | ToSIA02 | RF | ACPanel | - | PwrP | Mon | RA-ToSIA02:RF-ACPanel:PwrP-Mon | N/A | N/A
98 | Potência Q | RA | ToSIA02 | RF | ACPanel | - | PwrQ | Mon | RA-ToSIA02:RF-ACPanel:PwrQ-Mon | N/A | N/A
99 | Fator de potência | RA | ToSIA02 | RF | ACPanel | - | PwrFactor | Mon | RA-ToSIA02:RF-ACPanel:PwrFactor-Mon | N/A | N/A
100 | THD 1 | RA | ToSIA02 | RF | ACPanel | - | THD1 | Mon | RA-ToSIA02:RF-ACPanel:THD1-Mon | N/A | N/A
101 | THD 2 | RA | ToSIA02 | RF | ACPanel | - | THD2 | Mon | RA-ToSIA02:RF-ACPanel:THD2-Mon | N/A | N/A
102 | THD 3 | RA | ToSIA02 | RF | ACPanel | - | THD3 | Mon | RA-ToSIA02:RF-ACPanel:THD3-Mon | N/A | N/A
103 | Corrente Neutro | RA | ToSIA02 | RF | ACPanel | - | CurrentN | Mon | RA-ToSIA02:RF-ACPanel:CurrentN-Mon | N/A | N/A
104 | Frequencia | RA | ToSIA02 | RF | ACPanel | - | Freq | Mon | RA-ToSIA02:RF-ACPanel:Freq-Mon | N/A | N/A

## SSAmp Tower 01
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | AC da Torre 01 do Anel Sts | RA | ToSIA01 | RF | ACPanel | - | PwrACOp | Mon | RA-ToSIA01:RF-ACPanel:PwrACOp-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PwrACOpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_ACPanel_PwrACOpMon | .1
2 | AC das Fontes TDK Torre 01 Off | RA | ToSIA01 | RF | ACPanel | - | PwrACDsbl | Sel | RA-ToSIA01:RF-ACPanel:PwrACDsbl-Sel | N/A | N/A | RA_ToSIA01_RF_ACPanel_PwrACDsblSel | Digital | Control |  |  |  | RA_ToSIA01_RF_ACPanel_PwrACDsblSel | .1
3 | AC das Fontes TDK Torre 01 On | RA | ToSIA01 | RF | ACPanel | - | PwrACEnbl | Sel | RA-ToSIA01:RF-ACPanel:PwrACEnbl-Sel | N/A | N/A | RA_ToSIA01_RF_ACPanel_PwrACEnblSel | Digital | Control |  |  |  | RA_ToSIA01_RF_ACPanel_PwrACEnblSel | .1
4 | Falta de Fase do Painel Torre 01 do Anel | RA | ToSIA01 | RF | ACPanel | - | PhsFlt | Mon | RA-ToSIA01:RF-ACPanel:PhsFlt-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PhsFltMon | Digital | Output |  |  |  | RA_ToSIA01_RF_ACPanel_PhsFltMon | .1
5 | Interlock externo do Painel Torre 01 Para CLP | RA | ToSIA01 | RF | ACPanel | - | Intlk | Mon | RA-ToSIA01:RF-ACPanel:Intlk-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_IntlkMon | Digital | Input |  |  |  | RA_ToSIA01_RF_ACPanel_IntlkMon | .1
6 | Lê estado de Potência AC das Fontes TDK Torre 01 | RA | ToSIA01 | RF | ACPanel | - | PwrAC | Sts | RA-ToSIA01:RF-ACPanel:PwrAC-Sts | N/A | N/A | RA_ToSIA01_RF_ACPanel_PwrACSts | Digital | Input |  |  |  | RA_ToSIA01_RF_ACPanel_PwrACSts | .1
7 | PT-100 da Barra Dissipadora 01A | RA | ToSIA01 | RF | HeatSink | H01A | T | Mon | RA-ToSIA01:RF-HeatSink-H01A:T-Mon | RA-ToSIA01:RF-HeatSink-H01A:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H01A:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H01A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H01A_TMon | .5 | 2
8 | PT-100 da Barra Dissipadora 01B | RA | ToSIA01 | RF | HeatSink | H01B | T | Mon | RA-ToSIA01:RF-HeatSink-H01B:T-Mon | RA-ToSIA01:RF-HeatSink-H01B:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H01B:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H01B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H01B_TMon | .5 | 2
9 | PT-100 da Barra Dissipadora 02A | RA | ToSIA01 | RF | HeatSink | H02A | T | Mon | RA-ToSIA01:RF-HeatSink-H02A:T-Mon | RA-ToSIA01:RF-HeatSink-H02A:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H02A:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H02A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H02A_TMon | .5 | 2
10 | PT-100 da Barra Dissipadora 02B | RA | ToSIA01 | RF | HeatSink | H02B | T | Mon | RA-ToSIA01:RF-HeatSink-H02B:T-Mon | RA-ToSIA01:RF-HeatSink-H02B:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H02B:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H02B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H02B_TMon | .5 | 2
11 | PT-100 da Barra Dissipadora 03A | RA | ToSIA01 | RF | HeatSink | H03A | T | Mon | RA-ToSIA01:RF-HeatSink-H03A:T-Mon | RA-ToSIA01:RF-HeatSink-H03A:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H03A:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H03A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H03A_TMon | .5 | 2
12 | PT-100 da Barra Dissipadora 03B | RA | ToSIA01 | RF | HeatSink | H03B | T | Mon | RA-ToSIA01:RF-HeatSink-H03B:T-Mon | RA-ToSIA01:RF-HeatSink-H03B:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H03B:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H03B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H03B_TMon | .5 | 2
13 | PT-100 da Barra Dissipadora 04A | RA | ToSIA01 | RF | HeatSink | H04A | T | Mon | RA-ToSIA01:RF-HeatSink-H04A:T-Mon | RA-ToSIA01:RF-HeatSink-H04A:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H04A:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H04A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H04A_TMon | .5 | 2
14 | PT-100 da Barra Dissipadora 04B | RA | ToSIA01 | RF | HeatSink | H04B | T | Mon | RA-ToSIA01:RF-HeatSink-H04B:T-Mon | RA-ToSIA01:RF-HeatSink-H04B:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H04B:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H04B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H04B_TMon | .5 | 2
15 | PT-100 da Barra Dissipadora 05A | RA | ToSIA01 | RF | HeatSink | H05A | T | Mon | RA-ToSIA01:RF-HeatSink-H05A:T-Mon | RA-ToSIA01:RF-HeatSink-H05A:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H05A:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H05A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H05A_TMon | .5 | 2
16 | PT-100 da Barra Dissipadora 05B | RA | ToSIA01 | RF | HeatSink | H05B | T | Mon | RA-ToSIA01:RF-HeatSink-H05B:T-Mon | RA-ToSIA01:RF-HeatSink-H05B:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H05B:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H05B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H05B_TMon | .5 | 2
17 | PT-100 da Barra Dissipadora 06A | RA | ToSIA01 | RF | HeatSink | H06A | T | Mon | RA-ToSIA01:RF-HeatSink-H06A:T-Mon | RA-ToSIA01:RF-HeatSink-H06A:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H06A:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H06A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H06A_TMon | .5 | 2
18 | PT-100 da Barra Dissipadora 06B | RA | ToSIA01 | RF | HeatSink | H06B | T | Mon | RA-ToSIA01:RF-HeatSink-H06B:T-Mon | RA-ToSIA01:RF-HeatSink-H06B:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H06B:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H06B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H06B_TMon | .5 | 2
19 | PT-100 da Barra Dissipadora 07A | RA | ToSIA01 | RF | HeatSink | H07A | T | Mon | RA-ToSIA01:RF-HeatSink-H07A:T-Mon | RA-ToSIA01:RF-HeatSink-H07A:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H07A:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H07A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H07A_TMon | .5 | 2
20 | PT-100 da Barra Dissipadora 07B | RA | ToSIA01 | RF | HeatSink | H07B | T | Mon | RA-ToSIA01:RF-HeatSink-H07B:T-Mon | RA-ToSIA01:RF-HeatSink-H07B:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H07B:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H07B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H07B_TMon | .5 | 2
21 | PT-100 da Barra Dissipadora 08A | RA | ToSIA01 | RF | HeatSink | H08A | T | Mon | RA-ToSIA01:RF-HeatSink-H08A:T-Mon | RA-ToSIA01:RF-HeatSink-H08A:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H08A:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H08A_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H08A_TMon | .5 | 2
22 | PT-100 da Barra Dissipadora 08B | RA | ToSIA01 | RF | HeatSink | H08B | T | Mon | RA-ToSIA01:RF-HeatSink-H08B:T-Mon | RA-ToSIA01:RF-HeatSink-H08B:TUpperLimit-Cte | RA-ToSIA01:RF-HeatSink-H08B:TLowerLimit-Cte | RA_ToSIA01_RF_HeatSink_H08B_TMon | Analog | Input | Set_Temp[0] | Set_Temp[2] | C | RA_ToSIA01_RF_HeatSink_H08B_TMon | .5 | 2
23 | Temperatura abaixo do set Barra Dissipadora 01A | RA | ToSIA01 | RF | HeatSink | H01A | TDown | Mon | RA-ToSIA01:RF-HeatSink-H01A:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H01A_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H01A_TDownMon | .1
24 | Temperatura abaixo do set Barra Dissipadora 01B | RA | ToSIA01 | RF | HeatSink | H01B | TDown | Mon | RA-ToSIA01:RF-HeatSink-H01B:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H01B_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H01B_TDownMon | .1
25 | Temperatura abaixo do set Barra Dissipadora 02A | RA | ToSIA01 | RF | HeatSink | H02A | TDown | Mon | RA-ToSIA01:RF-HeatSink-H02A:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H02A_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H02A_TDownMon | .1
26 | Temperatura abaixo do set Barra Dissipadora 02B | RA | ToSIA01 | RF | HeatSink | H02B | TDown | Mon | RA-ToSIA01:RF-HeatSink-H02B:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H02B_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H02B_TDownMon | .1
27 | Temperatura abaixo do set Barra Dissipadora 03A | RA | ToSIA01 | RF | HeatSink | H03A | TDown | Mon | RA-ToSIA01:RF-HeatSink-H03A:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H03A_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H03A_TDownMon | .1
28 | Temperatura abaixo do set Barra Dissipadora 03B | RA | ToSIA01 | RF | HeatSink | H03B | TDown | Mon | RA-ToSIA01:RF-HeatSink-H03B:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H03B_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H03B_TDownMon | .1
29 | Temperatura abaixo do set Barra Dissipadora 04A | RA | ToSIA01 | RF | HeatSink | H04A | TDown | Mon | RA-ToSIA01:RF-HeatSink-H04A:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H04A_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H04A_TDownMon | .1
30 | Temperatura abaixo do set Barra Dissipadora 04B | RA | ToSIA01 | RF | HeatSink | H04B | TDown | Mon | RA-ToSIA01:RF-HeatSink-H04B:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H04B_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H04B_TDownMon | .1
31 | Temperatura abaixo do set Barra Dissipadora 05A | RA | ToSIA01 | RF | HeatSink | H05A | TDown | Mon | RA-ToSIA01:RF-HeatSink-H05A:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H05A_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H05A_TDownMon | .1
32 | Temperatura abaixo do set Barra Dissipadora 05B | RA | ToSIA01 | RF | HeatSink | H05B | TDown | Mon | RA-ToSIA01:RF-HeatSink-H05B:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H05B_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H05B_TDownMon | .1
33 | Temperatura abaixo do set Barra Dissipadora 06A | RA | ToSIA01 | RF | HeatSink | H06A | TDown | Mon | RA-ToSIA01:RF-HeatSink-H06A:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H06A_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H06A_TDownMon | .1
34 | Temperatura abaixo do set Barra Dissipadora 06B | RA | ToSIA01 | RF | HeatSink | H06B | TDown | Mon | RA-ToSIA01:RF-HeatSink-H06B:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H06B_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H06B_TDownMon | .1
35 | Temperatura abaixo do set Barra Dissipadora 07A | RA | ToSIA01 | RF | HeatSink | H07A | TDown | Mon | RA-ToSIA01:RF-HeatSink-H07A:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H07A_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H07A_TDownMon | .1
36 | Temperatura abaixo do set Barra Dissipadora 07B | RA | ToSIA01 | RF | HeatSink | H07B | TDown | Mon | RA-ToSIA01:RF-HeatSink-H07B:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H07B_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H07B_TDownMon | .1
37 | Temperatura abaixo do set Barra Dissipadora 08A | RA | ToSIA01 | RF | HeatSink | H08A | TDown | Mon | RA-ToSIA01:RF-HeatSink-H08A:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H08A_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H08A_TDownMon | .1
38 | Temperatura abaixo do set Barra Dissipadora 08B | RA | ToSIA01 | RF | HeatSink | H08B | TDown | Mon | RA-ToSIA01:RF-HeatSink-H08B:TDown-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H08B_TDownMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H08B_TDownMon | .1
39 | Temperatura acima do set Barra Dissipadora 01A | RA | ToSIA01 | RF | HeatSink | H01A | TUp | Mon | RA-ToSIA01:RF-HeatSink-H01A:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H01A_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H01A_TUpMon | .1
40 | Temperatura acima do set Barra Dissipadora 01B | RA | ToSIA01 | RF | HeatSink | H01B | TUp | Mon | RA-ToSIA01:RF-HeatSink-H01B:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H01B_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H01B_TUpMon | .1
41 | Temperatura acima do set Barra Dissipadora 02A | RA | ToSIA01 | RF | HeatSink | H02A | TUp | Mon | RA-ToSIA01:RF-HeatSink-H02A:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H02A_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H02A_TUpMon | .1
42 | Temperatura acima do set Barra Dissipadora 02B | RA | ToSIA01 | RF | HeatSink | H02B | TUp | Mon | RA-ToSIA01:RF-HeatSink-H02B:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H02B_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H02B_TUpMon | .1
43 | Temperatura acima do set Barra Dissipadora 03A | RA | ToSIA01 | RF | HeatSink | H03A | TUp | Mon | RA-ToSIA01:RF-HeatSink-H03A:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H03A_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H03A_TUpMon | .1
44 | Temperatura acima do set Barra Dissipadora 03B | RA | ToSIA01 | RF | HeatSink | H03B | TUp | Mon | RA-ToSIA01:RF-HeatSink-H03B:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H03B_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H03B_TUpMon | .1
45 | Temperatura acima do set Barra Dissipadora 04A | RA | ToSIA01 | RF | HeatSink | H04A | TUp | Mon | RA-ToSIA01:RF-HeatSink-H04A:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H04A_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H04A_TUpMon | .1
46 | Temperatura acima do set Barra Dissipadora 04B | RA | ToSIA01 | RF | HeatSink | H04B | TUp | Mon | RA-ToSIA01:RF-HeatSink-H04B:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H04B_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H04B_TUpMon | .1
47 | Temperatura acima do set Barra Dissipadora 05A | RA | ToSIA01 | RF | HeatSink | H05A | TUp | Mon | RA-ToSIA01:RF-HeatSink-H05A:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H05A_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H05A_TUpMon | .1
48 | Temperatura acima do set Barra Dissipadora 05B | RA | ToSIA01 | RF | HeatSink | H05B | TUp | Mon | RA-ToSIA01:RF-HeatSink-H05B:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H05B_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H05B_TUpMon | .1
49 | Temperatura acima do set Barra Dissipadora 06A | RA | ToSIA01 | RF | HeatSink | H06A | TUp | Mon | RA-ToSIA01:RF-HeatSink-H06A:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H06A_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H06A_TUpMon | .1
50 | Temperatura acima do set Barra Dissipadora 06B | RA | ToSIA01 | RF | HeatSink | H06B | TUp | Mon | RA-ToSIA01:RF-HeatSink-H06B:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H06B_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H06B_TUpMon | .1
51 | Temperatura acima do set Barra Dissipadora 07A | RA | ToSIA01 | RF | HeatSink | H07A | TUp | Mon | RA-ToSIA01:RF-HeatSink-H07A:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H07A_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H07A_TUpMon | .1
52 | Temperatura acima do set Barra Dissipadora 07B | RA | ToSIA01 | RF | HeatSink | H07B | TUp | Mon | RA-ToSIA01:RF-HeatSink-H07B:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H07B_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H07B_TUpMon | .1
53 | Temperatura acima do set Barra Dissipadora 08A | RA | ToSIA01 | RF | HeatSink | H08A | TUp | Mon | RA-ToSIA01:RF-HeatSink-H08A:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H08A_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H08A_TUpMon | .1
54 | Temperatura acima do set Barra Dissipadora 08B | RA | ToSIA01 | RF | HeatSink | H08B | TUp | Mon | RA-ToSIA01:RF-HeatSink-H08B:TUp-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H08B_TUpMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H08B_TUpMon | .1
55 | Termostato da Barra Dissipadora 01A | RA | ToSIA01 | RF | HeatSink | H01A | Tms | Mon | RA-ToSIA01:RF-HeatSink-H01A:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H01A_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H01A_TmsMon | .1
56 | Termostato da Barra Dissipadora 01B | RA | ToSIA01 | RF | HeatSink | H01B | Tms | Mon | RA-ToSIA01:RF-HeatSink-H01B:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H01B_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H01B_TmsMon | .1
57 | Termostato da Barra Dissipadora 02A | RA | ToSIA01 | RF | HeatSink | H02A | Tms | Mon | RA-ToSIA01:RF-HeatSink-H02A:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H02A_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H02A_TmsMon | .1
58 | Termostato da Barra Dissipadora 02B | RA | ToSIA01 | RF | HeatSink | H02B | Tms | Mon | RA-ToSIA01:RF-HeatSink-H02B:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H02B_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H02B_TmsMon | .1
59 | Termostato da Barra Dissipadora 03A | RA | ToSIA01 | RF | HeatSink | H03A | Tms | Mon | RA-ToSIA01:RF-HeatSink-H03A:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H03A_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H03A_TmsMon | .1
60 | Termostato da Barra Dissipadora 03B | RA | ToSIA01 | RF | HeatSink | H03B | Tms | Mon | RA-ToSIA01:RF-HeatSink-H03B:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H03B_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H03B_TmsMon | .1
61 | Termostato da Barra Dissipadora 04A | RA | ToSIA01 | RF | HeatSink | H04A | Tms | Mon | RA-ToSIA01:RF-HeatSink-H04A:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H04A_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H04A_TmsMon | .1
62 | Termostato da Barra Dissipadora 04B | RA | ToSIA01 | RF | HeatSink | H04B | Tms | Mon | RA-ToSIA01:RF-HeatSink-H04B:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H04B_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H04B_TmsMon | .1
63 | Termostato da Barra Dissipadora 05A | RA | ToSIA01 | RF | HeatSink | H05A | Tms | Mon | RA-ToSIA01:RF-HeatSink-H05A:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H05A_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H05A_TmsMon | .1
64 | Termostato da Barra Dissipadora 05B | RA | ToSIA01 | RF | HeatSink | H05B | Tms | Mon | RA-ToSIA01:RF-HeatSink-H05B:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H05B_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H05B_TmsMon | .1
65 | Termostato da Barra Dissipadora 06A | RA | ToSIA01 | RF | HeatSink | H06A | Tms | Mon | RA-ToSIA01:RF-HeatSink-H06A:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H06A_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H06A_TmsMon | .1
66 | Termostato da Barra Dissipadora 06B | RA | ToSIA01 | RF | HeatSink | H06B | Tms | Mon | RA-ToSIA01:RF-HeatSink-H06B:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H06B_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H06B_TmsMon | .1
67 | Termostato da Barra Dissipadora 07A | RA | ToSIA01 | RF | HeatSink | H07A | Tms | Mon | RA-ToSIA01:RF-HeatSink-H07A:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H07A_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H07A_TmsMon | .1
68 | Termostato da Barra Dissipadora 07B | RA | ToSIA01 | RF | HeatSink | H07B | Tms | Mon | RA-ToSIA01:RF-HeatSink-H07B:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H07B_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H07B_TmsMon | .1
69 | Termostato da Barra Dissipadora 08A | RA | ToSIA01 | RF | HeatSink | H08A | Tms | Mon | RA-ToSIA01:RF-HeatSink-H08A:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H08A_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H08A_TmsMon | .1
70 | Termostato da Barra Dissipadora 08B | RA | ToSIA01 | RF | HeatSink | H08B | Tms | Mon | RA-ToSIA01:RF-HeatSink-H08B:Tms-Mon | N/A | N/A | RA_ToSIA01_RF_HeatSink_H08B_TmsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_HeatSink_H08B_TmsMon | .1
71 | Interlock Geral SSA 1 | RA | ToSIA01 | RF | SSAmpTower | - | Sts | Mon | RA-ToSIA01:RF-SSAmpTower:Sts-Mon | N/A | N/A | RA_ToSIA01_RF_SSAmpTower_StsMon | Digital | Input |  |  |  | RA_ToSIA01_RF_SSAmpTower_StsMon | .1
72 | Rotâmetro Torre 01 do Anel | RA | ToSIA01 | RF | SSAmpTower | - | HdFlwRt | Mon | RA-ToSIA01:RF-SSAmpTower:HdFlwRt-Mon | N/A | N/A | RA_ToSIA01_RF_SSAmpTower_HdFlwRtMon | Digital | Input |  |  |  | RA_ToSIA01_RF_SSAmpTower_HdFlwRtMon | .1
73 | 48V das Fontes TDK Torre 01 Off | RA | ToSIA01 | RF | TDKSource | - | PwrDCDsbl | Sel | RA-ToSIA01:RF-TDKSource:PwrDCDsbl-Sel | N/A | N/A | RA_ToSIA01_RF_TDKSource_PwrDCDsblSel | Digital | Control |  |  |  | RA_ToSIA01_RF_TDKSource_PwrDCDsblSel | .1
74 | 48V das Fontes TDK Torre 01 On | RA | ToSIA01 | RF | TDKSource | - | PwrDCEnbl | Sel | RA-ToSIA01:RF-TDKSource:PwrDCEnbl-Sel | N/A | N/A | RA_ToSIA01_RF_TDKSource_PwrDCEnblSel | Digital | Control |  |  |  | RA_ToSIA01_RF_TDKSource_PwrDCEnblSel | .1
75 | 48V das Fontes TDK Torre 01 Sts | RA | ToSIA01 | RF | TDKSource | - | PwrDC | Sts | RA-ToSIA01:RF-TDKSource:PwrDC-Sts | N/A | N/A | RA_ToSIA01_RF_TDKSource_PwrDCSts | Digital | Input |  |  |  | RA_ToSIA01_RF_TDKSource_PwrDCSts | .1
76 | Falha Ac Mini Rack 1 Torre 1 | RA | ToSIA01 | RF | TDKSource | R1 | StsAC | Mon | RA-ToSIA01:RF-TDKSource-R1:StsAC-Mon | N/A | N/A | RA_ToSIA01_RF_TDKSource_R1_StsACMon | Digital | Input |  |  |  | RA_ToSIA01_RF_TDKSource_R1_StsACMon | .1
77 | Falha Ac Mini Rack 2 Torre 1 | RA | ToSIA01 | RF | TDKSource | R2 | StsAC | Mon | RA-ToSIA01:RF-TDKSource-R2:StsAC-Mon | N/A | N/A | RA_ToSIA01_RF_TDKSource_R2_StsACMon | Digital | Input |  |  |  | RA_ToSIA01_RF_TDKSource_R2_StsACMon | .1
78 | Falha Ac Mini Rack 3 Torre 1 | RA | ToSIA01 | RF | TDKSource | R3 | StsAC | Mon | RA-ToSIA01:RF-TDKSource-R3:StsAC-Mon | N/A | N/A | RA_ToSIA01_RF_TDKSource_R3_StsACMon | Digital | Input |  |  |  | RA_ToSIA01_RF_TDKSource_R3_StsACMon | .1
79 | Falha Ac Mini Rack 4 Torre 1 | RA | ToSIA01 | RF | TDKSource | R4 | StsAC | Mon | RA-ToSIA01:RF-TDKSource-R4:StsAC-Mon | N/A | N/A | RA_ToSIA01_RF_TDKSource_R4_StsACMon | Digital | Input |  |  |  | RA_ToSIA01_RF_TDKSource_R4_StsACMon | .1
80 | Interlock externo do CLP para Painel Torre 01 (Saída) | SI | 02SB | RF | Intlk | - | IntlkACPanel01 | Mon | SI-02SB:RF-Intlk:IntlkACPanel01-Mon | N/A | N/A | SI_02SB_RF_Intlk_IntlkACPanel01Mon | Digital | Input |  |  |  | SI_02SB_RF_Intlk_IntlkACPanel01Mon | .1
81 | Torre 1 Enbl | RA | ToSIA01 | RF | SSAmpTower | - | Enbl | Sel | RA-ToSIA01:RF-SSAmpTower:Enbl-Sel | N/A | N/A | RA_ToSIA01_RF_SSAmpTower_EnblSel | Digital | Control |  |  |  | RA_ToSIA01_RF_SSAmpTower_EnblSel | .1
82 | Torre 1 Enbl Sts | RA | ToSIA01 | RF | SSAmpTower | - | Enbl | Sts | RA-ToSIA01:RF-SSAmpTower:Enbl-Sts | N/A | N/A | RA_ToSIA01_RF_SSAmpTower_EnblSts | Digital | Input |  |  |  | RA_ToSIA01_RF_SSAmpTower_EnblSts | .1
83 | Temperatura Minirack 01 | RA | ToSIA01 | RF | SSAMux | 1 | T | Mon | RA-ToSIA01:RF-SSAMux-1:T-Mon | N/A | N/A | RA_ToSIA01_RF_Mux_1_TMon | Analog | Input |  |  | C | RA_ToSIA01_RF_Mux_1_TMon | .5
84 | Temperatura Minirack 02 | RA | ToSIA01 | RF | SSAMux | 2 | T | Mon | RA-ToSIA01:RF-SSAMux-2:T-Mon | N/A | N/A | RA_ToSIA01_RF_Mux_2_TMon | Analog | Input |  |  | C | RA_ToSIA01_RF_Mux_2_TMon | .5
85 | Temperatura Minirack 03 | RA | ToSIA01 | RF | SSAMux | 3 | T | Mon | RA-ToSIA01:RF-SSAMux-3:T-Mon | N/A | N/A | RA_ToSIA01_RF_Mux_3_TMon | Analog | Input |  |  | C | RA_ToSIA01_RF_Mux_3_TMon | .5
86 | Temperatura Minirack 04 | RA | ToSIA01 | RF | SSAMux | 4 | T | Mon | RA-ToSIA01:RF-SSAMux-4:T-Mon | N/A | N/A | RA_ToSIA01_RF_Mux_4_TMon | Analog | Input |  |  | C | RA_ToSIA01_RF_Mux_4_TMon | .5
87 | Corrente de Fase 1 | RA | ToSIA01 | RF | ACPanel | - | PhsCurrent1 | Mon | RA-ToSIA01:RF-ACPanel:PhsCurrent1-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PhsCurrent1Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_PhsCurrent1Mon
88 | Corrente de Fase 2 | RA | ToSIA01 | RF | ACPanel | - | PhsCurrent2 | Mon | RA-ToSIA01:RF-ACPanel:PhsCurrent2-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PhsCurrent2Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_PhsCurrent2Mon
89 | Corrente de Fase 3 | RA | ToSIA01 | RF | ACPanel | - | PhsCurrent3 | Mon | RA-ToSIA01:RF-ACPanel:PhsCurrent3-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PhsCurrent3Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_PhsCurrent3Mon
90 | Tensão Fase 1 | RA | ToSIA01 | RF | ACPanel | - | PhsVoltage1 | Mon | RA-ToSIA01:RF-ACPanel:PhsVoltage1-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PhsVoltage1Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_PhsVoltage1Mon
91 | Tensão Fase 2 | RA | ToSIA01 | RF | ACPanel | - | PhsVoltage2 | Mon | RA-ToSIA01:RF-ACPanel:PhsVoltage2-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PhsVoltage2Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_PhsVoltage2Mon
92 | Tensão Fase 3 | RA | ToSIA01 | RF | ACPanel | - | PhsVoltage3 | Mon | RA-ToSIA01:RF-ACPanel:PhsVoltage3-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PhsVoltage3Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_PhsVoltage3Mon
93 | Tensão de linha 12 | RA | ToSIA01 | RF | ACPanel | - | LineVoltage12 | Mon | RA-ToSIA01:RF-ACPanel:LineVoltage12-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_LineVoltage12Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_LineVoltage12Mon
94 | Tensão de linha 13 | RA | ToSIA01 | RF | ACPanel | - | LineVoltage13 | Mon | RA-ToSIA01:RF-ACPanel:LineVoltage13-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_LineVoltage13Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_LineVoltage13Mon
95 | Tensão de linha 23 | RA | ToSIA01 | RF | ACPanel | - | LineVoltage23 | Mon | RA-ToSIA01:RF-ACPanel:LineVoltage23-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_LineVoltage23Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_LineVoltage23Mon
96 | Potência S | RA | ToSIA01 | RF | ACPanel | - | PwrS | Mon | RA-ToSIA01:RF-ACPanel:PwrS-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PwrSMon | [5 empty] | RA_ToSIA01_RF_ACPanel_PwrSMon
97 | Potencia P | RA | ToSIA01 | RF | ACPanel | - | PwrP | Mon | RA-ToSIA01:RF-ACPanel:PwrP-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PwrPMon | [5 empty] | RA_ToSIA01_RF_ACPanel_PwrPMon
98 | Potência Q | RA | ToSIA01 | RF | ACPanel | - | PwrQ | Mon | RA-ToSIA01:RF-ACPanel:PwrQ-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PwrQMon | [5 empty] | RA_ToSIA01_RF_ACPanel_PwrQMon
99 | Fator de potência | RA | ToSIA01 | RF | ACPanel | - | PwrFactor | Mon | RA-ToSIA01:RF-ACPanel:PwrFactor-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_PwrFactorMon | [5 empty] | RA_ToSIA01_RF_ACPanel_PwrFactorMon
100 | THD 1 | RA | ToSIA01 | RF | ACPanel | - | THD1 | Mon | RA-ToSIA01:RF-ACPanel:THD1-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_THD1Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_THD1Mon
101 | THD 2 | RA | ToSIA01 | RF | ACPanel | - | THD2 | Mon | RA-ToSIA01:RF-ACPanel:THD2-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_THD2Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_THD2Mon
102 | THD 3 | RA | ToSIA01 | RF | ACPanel | - | THD3 | Mon | RA-ToSIA01:RF-ACPanel:THD3-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_THD3Mon | [5 empty] | RA_ToSIA01_RF_ACPanel_THD3Mon
103 | Corrente Neutro | RA | ToSIA01 | RF | ACPanel | - | CurrentN | Mon | RA-ToSIA01:RF-ACPanel:CurrentN-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_CurrentNMon | [5 empty] | RA_ToSIA01_RF_ACPanel_CurrentNMon
104 | Frequencia | RA | ToSIA01 | RF | ACPanel | - | Freq | Mon | RA-ToSIA01:RF-ACPanel:Freq-Mon | N/A | N/A | RA_ToSIA01_RF_ACPanel_FreqMon | [5 empty] | RA_ToSIA01_RF_ACPanel_FreqMon

## Transmission Line
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Detector de Arco Circulador | RA | TLSIA | RF | Circulator | - | Arc | Mon | RA-TLSIA:RF-Circulator:Arc-Mon |  |  | RA_TLSIA_RF_Circulator_Arc_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Circulator_Arc_Mon | .1
2 | Detector de Arco Carga 300 kW | RA | TLSIA | RF | Load | - | Arc | Mon | RA-TLSIA:RF-Load:Arc-Mon |  |  | RA_TLSIA_RF_Load_Arc_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Load_Arc_Mon | .1
3 | Teste detector de Arco Circulador | RA | RaSIA02 | RF | ArcDetec | Circ | Test | Sel | RA-RaSIA02:RF-ArcDetec-Circ:Test-Sel |  |  | RA_RaSIA02_RF_ArcDetec_Circ_TestSel | Digital | Control |  |  |  | RA_RaSIA02_RF_ArcDetec_Circ_TestSel | .1
4 | Teste detector de Arco Carga 300 kW | RA | RaSIA02 | RF | ArcDetec | Load | Test | Sel | RA-RaSIA02:RF-ArcDetec-Load:Test-Sel |  |  | RA_RaSIA02_RF_ArcDetec_Load_TestSel | Digital | Control |  |  |  | RA_RaSIA02_RF_ArcDetec_Load_TestSel | .1
5 | Leitura Teste Detector de Arco Circulador | RA | RaSIA02 | RF | ArcDetec | Circ | Test | Sts | RA-RaSIA02:RF-ArcDetec-Circ:Test-Sts |  |  | RA_RaSIA02_RF_ArcDetec_Circ_TestSts | Digital | Output |  |  |  | RA_RaSIA02_RF_ArcDetec_Circ_TestSts | .1
6 | Leitura Teste Detector de Arco Carga 300 kW | RA | RaSIA02 | RF | ArcDetec | Load | Test | Sts | RA-RaSIA02:RF-ArcDetec-Load:Test-Sts |  |  | RA_RaSIA02_RF_ArcDetec_Load_TestSts | Digital | Output |  |  |  | RA_RaSIA02_RF_ArcDetec_Load_TestSts | .1
7 | Sistema de Interlock circulador operacional | RA | TLSIA | RF | Circulator | - | IntlkOp | Mon | RA-TLSIA:RF-Circulator:IntlkOp-Mon |  |  | RA_TLSIA_RF_Circulator_IntlkOp_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Circulator_IntlkOp_Mon | .1
8 | Vazão Circulador - Via Skid | RA | TLSIA | RF | Circulator | - | FlwRt | Mon | RA-TLSIA:RF-Circulator:FlwRt-Mon |  |  | RA_TLSIA_RF_Circulator_FlwRt_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Circulator_FlwRt_Mon | .1
9 | Bobinas do circulador | RA | TLSIA | RF | Circulator | - | Sts | Mon | RA-TLSIA:RF-Circulator:Sts-Mon |  |  | RA_TLSIA_RF_Circulator_Sts_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Circulator_Sts_Mon | .1
10 | Temp. do Circulador Abaixo do Set | RA | TLSIA | RF | Circulator | - | TinDown | Mon | RA-TLSIA:RF-Circulator:TinDown-Mon |  |  | RA_TLSIA_RF_Circulator_TinDown_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Circulator_TinDown_Mon | .1
11 | Temp. do Circulador Acima do Set | RA | TLSIA | RF | Circulator | - | TinUp | Mon | RA-TLSIA:RF-Circulator:TinUp-Mon |  |  | RA_TLSIA_RF_Circulator_TinUp_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Circulator_TinUp_Mon | .1
12 | Drift de Temp muito Alto | RA | TLSIA | RF | Circulator | - | TDrift | Mon | RA-TLSIA:RF-Circulator:TDrift-Mon |  |  | RA_TLSIA_RF_Circulator_TDrift_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Circulator_TDrift_Mon | .1
13 | Temp. Ambiente Abaixo do Set | RA | TLSIA | RF | Circulator | - | TEnv | Mon | RA-TLSIA:RF-Circulator:TEnv-Mon |  |  | RA_TLSIA_RF_Circulator_TEnv_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Circulator_TEnv_Mon | .1
14 | Vazão Carga 300kW | RA | TLSIA | RF | Load | - | FlwRt | Mon | RA-TLSIA:RF-Load:FlwRt-Mon |  |  | RA_TLSIA_RF_Load_FlwRt_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_Load_FlwRt_Mon | .1
15 | Interlock geral Linha de Transmissao | RA | TLSIA | RF | TrLine | - | Sts | Mon | RA-TLSIA:RF-TrLine:Sts-Mon |  |  | RA_TLSIA_RF_TrLine_Sts_Mon | Digital | Input |  |  |  | RA_TLSIA_RF_TrLine_Sts_Mon | .1
16 | Reset Detector de Arco Circulador | RA | RaSIA02 | RF | ArcDetec | Circ | Reset | Mon | RA-RaSIA02:RF-ArcDetec-Circ:Reset-Mon |  |  | RA_RaSIA02_RF_ArcDetec_Circ_ResetMon | Digital | Input |  |  |  | RA_RaSIA02_RF_ArcDetec_Circ_ResetMon | .1
17 | Reset Detector de Arco Carga 300kW | RA | RaSIA02 | RF | ArcDetec | Load | Reset | Mon | RA-RaSIA02:RF-ArcDetec-Load:Reset-Mon |  |  | RA_RaSIA02_RF_ArcDetec_Load_ResetMon | Digital | Input |  |  |  | RA_RaSIA02_RF_ArcDetec_Load_ResetMon | .1
18 | Potencia na carga | RA | TLSIA | RF | Circulator | - | PwrRevIndBm | Mon | RA-TLSIA:RF-Circulator:PwrRevIndBm-Mon
19 | Combinador | RA | TLSIA | RF | Combiner | - | T | Mon | RA-TLSIA:RF-Combiner:T-Mon |  |  | RA_TLSIA_RF_Combiner_T_Mon | Analog | Input |  |  |  | RA_TLSIA_RF_Combiner_T_Mon | .5
20 | Detector de Arco Power Fail Out | RA | RaSIA02 | RF | ArcDetec | Circ | PwrFail | Mon | RA-RaSIA02:RF-ArcDetec-Circ:PwrFail-Mon |  |  | RA_RaSIA02_RF_ArcDetec_Circ_PwrFailMon | Digital | Input |  |  |  | RA_RaSIA02_RF_ArcDetec_Circ_PwrFailMon | .1
21 | Detector de Arco Power Fail Out | RA | RaSIA02 | RF | ArcDetec | Load | PwrFail | Mon | RA-RaSIA02:RF-ArcDetec-Load:PwrFail-Mon |  |  | RA_RaSIA02_RF_ArcDetec_Load_PwrFailMon | Digital | Input |  |  |  | RA_RaSIA02_RF_ArcDetec_Load_PwrFailMon | .1

## Petra 7
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Vácuo Petra VII | SI | 02SB | RF | P7Cav | - | Pressure | Mon | SI-02SB:RF-P7Cav:Pressure-Mon | N/A | N/A | SI_02SB_RF_P7Cav_PressureMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_PressureMon | .1
2 | Chave de Fluxo 01 Petra VII | SI | 02SB | RF | P7Cav | - | HDFlwRt1 | Mon | SI-02SB:RF-P7Cav:HDFlwRt1-Mon | N/A | N/A | SI_02SB_RF_P7Cav_HDFlwRt1Mon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_HDFlwRt1Mon | .1
3 | Chave de Fluxo 02 Petra VII | SI | 02SB | RF | P7Cav | - | HDFlwRt2 | Mon | SI-02SB:RF-P7Cav:HDFlwRt2-Mon | N/A | N/A | SI_02SB_RF_P7Cav_HDFlwRt2Mon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_HDFlwRt2Mon | .1
4 | Chave de Fluxo 03 Petra VII | SI | 02SB | RF | P7Cav | - | HDFlwRt3 | Mon | SI-02SB:RF-P7Cav:HDFlwRt3-Mon | N/A | N/A | SI_02SB_RF_P7Cav_HDFlwRt3Mon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_HDFlwRt3Mon | .1
5 | Sensor de Pressão do Acoplador | SI | 02SB | RF | P7Cav | - | CoupPressure | Mon | SI-02SB:RF-P7Cav:CoupPressure-Mon | N/A | N/A | SI_02SB_RF_P7Cav_CoupPressureMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_CoupPressureMon | .1
6 | PT - 100 Cilindro 01 PetraVII | SI | 02SB | RF | P7Cav | - | Cylin1T | Mon | SI-02SB:RF-P7Cav:Cylin1T-Mon | SI-02SB:RF-P7Cav:Cylin1TUpperLimit-Cte | SI-02SB:RF-P7Cav:Cylin1TLowerLimit-Cte | SI_02SB_RF_P7Cav_Cylin1TMon | Analog | Input | Set_Temp[1] | Set_Temp[3] | C | SI_02SB_RF_P7Cav_Cylin1TMon | .5 | 2
7 | PT - 100 Cilindro 02 PetraVII | SI | 02SB | RF | P7Cav | - | Cylin2T | Mon | SI-02SB:RF-P7Cav:Cylin2T-Mon | SI-02SB:RF-P7Cav:Cylin2TUpperLimit-Cte | SI-02SB:RF-P7Cav:Cylin2TLowerLimit-Cte | SI_02SB_RF_P7Cav_Cylin2TMon | Analog | Input | Set_Temp[1] | Set_Temp[3] | C | SI_02SB_RF_P7Cav_Cylin2TMon | .5 | 2
8 | PT - 100 Cilindro 03 PetraVII | SI | 02SB | RF | P7Cav | - | Cylin3T | Mon | SI-02SB:RF-P7Cav:Cylin3T-Mon | SI-02SB:RF-P7Cav:Cylin3TUpperLimit-Cte | SI-02SB:RF-P7Cav:Cylin3TLowerLimit-Cte | SI_02SB_RF_P7Cav_Cylin3TMon | Analog | Input | Set_Temp[1] | Set_Temp[3] | C | SI_02SB_RF_P7Cav_Cylin3TMon | .5 | 2
9 | PT - 100 Cilindro 04 PetraVII | SI | 02SB | RF | P7Cav | - | Cylin4T | Mon | SI-02SB:RF-P7Cav:Cylin4T-Mon | SI-02SB:RF-P7Cav:Cylin4TUpperLimit-Cte | SI-02SB:RF-P7Cav:Cylin4TLowerLimit-Cte | SI_02SB_RF_P7Cav_Cylin4TMon | Analog | Input | Set_Temp[1] | Set_Temp[3] | C | SI_02SB_RF_P7Cav_Cylin4TMon | .5 | 2
10 | PT - 100 Cilindro 05 PetraVII | SI | 02SB | RF | P7Cav | - | Cylin5T | Mon | SI-02SB:RF-P7Cav:Cylin5T-Mon | SI-02SB:RF-P7Cav:Cylin5TUpperLimit-Cte | SI-02SB:RF-P7Cav:Cylin5TLowerLimit-Cte | SI_02SB_RF_P7Cav_Cylin5TMon | Analog | Input | Set_Temp[1] | Set_Temp[3] | C | SI_02SB_RF_P7Cav_Cylin5TMon | .5 | 2
11 | PT - 100 Cilindro 06 PetraVII | SI | 02SB | RF | P7Cav | - | Cylin6T | Mon | SI-02SB:RF-P7Cav:Cylin6T-Mon | SI-02SB:RF-P7Cav:Cylin6TUpperLimit-Cte | SI-02SB:RF-P7Cav:Cylin6TLowerLimit-Cte | SI_02SB_RF_P7Cav_Cylin6TMon | Analog | Input | Set_Temp[1] | Set_Temp[3] | C | SI_02SB_RF_P7Cav_Cylin6TMon | .5 | 2
12 | PT - 100 Cilindro 07 PetraVII | SI | 02SB | RF | P7Cav | - | Cylin7T | Mon | SI-02SB:RF-P7Cav:Cylin7T-Mon | SI-02SB:RF-P7Cav:Cylin7TUpperLimit-Cte | SI-02SB:RF-P7Cav:Cylin7TLowerLimit-Cte | SI_02SB_RF_P7Cav_Cylin7TMon | Analog | Input | Set_Temp[1] | Set_Temp[3] | C | SI_02SB_RF_P7Cav_Cylin7TMon | .5 | 2
13 | Temperatura do Acoplador Petra VII | SI | 02SB | RF | P7Cav | - | CoupT | Mon | SI-02SB:RF-P7Cav:CoupT-Mon | SI-02SB:RF-P7Cav:CoupTUpperLimit-Cte | SI-02SB:RF-P7Cav:CoupTLowerLimit-Cte | SI_02SB_RF_P7Cav_CoupTMon | Analog | Input | Set_Temp[7] | Set_Temp[3] | C | SI_02SB_RF_P7Cav_CoupTMon | .5 | 2
14 | Interlock Geral Petra 7 | SI | 02SB | RF | P7Cav | - | Sts | Mon | SI-02SB:RF-P7Cav:Sts-Mon | N/A | N/A | SI_02SB_RF_P7Cav_StsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_StsMon | .1
15 | PT - 100 Acoplador Abaixo do Set | SI | 02SB | RF | P7Cav | - | CoupTDown | Mon | SI-02SB:RF-P7Cav:CoupTDown-Mon | N/A | N/A | SI_02SB_RF_P7Cav_CoupTDownMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_CoupTDownMon | .1
16 | PT - 100 Acoplador Acima do Set | SI | 02SB | RF | P7Cav | - | CoupTUp | Mon | SI-02SB:RF-P7Cav:CoupTUp-Mon | N/A | N/A | SI_02SB_RF_P7Cav_CoupTUpMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_CoupTUpMon | .1
17 | PT100 Cilindro 01 Abaixo do Set | SI | 02SB | RF | P7Cav | - | Cylin1TDown | Mon | SI-02SB:RF-P7Cav:Cylin1TDown-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin1TDownMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin1TDownMon | .1
18 | PT100 Cilindro 02 Abaixo do Set | SI | 02SB | RF | P7Cav | - | Cylin2TDown | Mon | SI-02SB:RF-P7Cav:Cylin2TDown-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin2TDownMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin2TDownMon | .1
19 | PT100 Cilindro 03 Abaixo do Set | SI | 02SB | RF | P7Cav | - | Cylin3TDown | Mon | SI-02SB:RF-P7Cav:Cylin3TDown-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin3TDownMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin3TDownMon | .1
20 | PT100 Cilindro 04 Abaixo do Set | SI | 02SB | RF | P7Cav | - | Cylin4TDown | Mon | SI-02SB:RF-P7Cav:Cylin4TDown-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin4TDownMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin4TDownMon | .1
21 | PT100 Cilindro 05 Abaixo do Set | SI | 02SB | RF | P7Cav | - | Cylin5TDown | Mon | SI-02SB:RF-P7Cav:Cylin5TDown-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin5TDownMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin5TDownMon | .1
22 | PT100 Cilindro 06 Abaixo do Set | SI | 02SB | RF | P7Cav | - | Cylin6TDown | Mon | SI-02SB:RF-P7Cav:Cylin6TDown-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin6TDownMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin6TDownMon | .1
23 | PT100 Cilindro 07 Abaixo do Set | SI | 02SB | RF | P7Cav | - | Cylin7TDown | Mon | SI-02SB:RF-P7Cav:Cylin7TDown-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin7TDownMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin7TDownMon | .1
24 | PT100 Cilindro 01 Acima do Set | SI | 02SB | RF | P7Cav | - | Cylin1TUp | Mon | SI-02SB:RF-P7Cav:Cylin1TUp-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin1TUpMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin1TUpMon | .1
25 | PT100 Cilindro 02 Acima do Set | SI | 02SB | RF | P7Cav | - | Cylin2TUp | Mon | SI-02SB:RF-P7Cav:Cylin2TUp-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin2TUpMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin2TUpMon | .1
26 | PT100 Cilindro 03 Acima do Set | SI | 02SB | RF | P7Cav | - | Cylin3TUp | Mon | SI-02SB:RF-P7Cav:Cylin3TUp-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin3TUpMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin3TUpMon | .1
27 | PT100 Cilindro 04 Acima do Set | SI | 02SB | RF | P7Cav | - | Cylin4TUp | Mon | SI-02SB:RF-P7Cav:Cylin4TUp-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin4TUpMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin4TUpMon | .1
28 | PT100 Cilindro 05 Acima do Set | SI | 02SB | RF | P7Cav | - | Cylin5TUp | Mon | SI-02SB:RF-P7Cav:Cylin5TUp-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin5TUpMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin5TUpMon | .1
29 | PT100 Cilindro 06 Acima do Set | SI | 02SB | RF | P7Cav | - | Cylin6TUp | Mon | SI-02SB:RF-P7Cav:Cylin6TUp-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin6TUpMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin6TUpMon | .1
30 | PT100 Cilindro 07 Acima do Set | SI | 02SB | RF | P7Cav | - | Cylin7TUp | Mon | SI-02SB:RF-P7Cav:Cylin7TUp-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin7TUpMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin7TUpMon | .1
29 | Termostato Disco 01 | SI | 02SB | RF | P7Cav | - | Disc1Tms | Mon | SI-02SB:RF-P7Cav:Disc1Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Disc1TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Disc1TmsMon | .1
30 | Termostato Disco 02 | SI | 02SB | RF | P7Cav | - | Disc2Tms | Mon | SI-02SB:RF-P7Cav:Disc2Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Disc2TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Disc2TmsMon | .1
31 | Termostato Disco 03 | SI | 02SB | RF | P7Cav | - | Disc3Tms | Mon | SI-02SB:RF-P7Cav:Disc3Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Disc3TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Disc3TmsMon | .1
32 | Termostato Disco 04 | SI | 02SB | RF | P7Cav | - | Disc4Tms | Mon | SI-02SB:RF-P7Cav:Disc4Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Disc4TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Disc4TmsMon | .1
33 | Termostato Disco 05 | SI | 02SB | RF | P7Cav | - | Disc5Tms | Mon | SI-02SB:RF-P7Cav:Disc5Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Disc5TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Disc5TmsMon | .1
34 | Termostato Disco 06 | SI | 02SB | RF | P7Cav | - | Disc6Tms | Mon | SI-02SB:RF-P7Cav:Disc6Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Disc6TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Disc6TmsMon | .1
35 | Termostato Disco 07 | SI | 02SB | RF | P7Cav | - | Disc7Tms | Mon | SI-02SB:RF-P7Cav:Disc7Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Disc7TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Disc7TmsMon | .1
36 | Termostato Disco 08 | SI | 02SB | RF | P7Cav | - | Disc8Tms | Mon | SI-02SB:RF-P7Cav:Disc8Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Disc8TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Disc8TmsMon | .1
37 | Termostato Cilindro 01 | SI | 02SB | RF | P7Cav | - | Cylin1Tms | Mon | SI-02SB:RF-P7Cav:Cylin1Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin1TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin1TmsMon | .1
38 | Termostato Cilindro 02 | SI | 02SB | RF | P7Cav | - | Cylin2Tms | Mon | SI-02SB:RF-P7Cav:Cylin2Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin2TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin2TmsMon | .1
39 | Termostato Cilindro 03 | SI | 02SB | RF | P7Cav | - | Cylin3Tms | Mon | SI-02SB:RF-P7Cav:Cylin3Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin3TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin3TmsMon | .1
40 | Termostato Cilindro 04 | SI | 02SB | RF | P7Cav | - | Cylin4Tms | Mon | SI-02SB:RF-P7Cav:Cylin4Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin4TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin4TmsMon | .1
41 | Termostato Cilindro 05 | SI | 02SB | RF | P7Cav | - | Cylin5Tms | Mon | SI-02SB:RF-P7Cav:Cylin5Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin5TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin5TmsMon | .1
42 | Termostato Cilindro 06 | SI | 02SB | RF | P7Cav | - | Cylin6Tms | Mon | SI-02SB:RF-P7Cav:Cylin6Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin6TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin6TmsMon | .1
43 | Termostato Cilindro 07 | SI | 02SB | RF | P7Cav | - | Cylin7Tms | Mon | SI-02SB:RF-P7Cav:Cylin7Tms-Mon | N/A | N/A | SI_02SB_RF_P7Cav_Cylin7TmsMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_Cylin7TmsMon | .1
44 | Potencia RF para o Interlock | SI | 02SB | RF | P7Cav | - | PwrRFIntlk | Mon | SI-02SB:RF-P7Cav:PwrRFIntlk-Mon | N/A | N/A | SI_02SB_RF_P7Cav_PwrRFIntlkMon | Analog | Input | N/A | N/A | dBm | SI_02SB_RF_P7Cav_PwrRFIntlkMon | .5 | 3
45 | PT - 100 Janela de Quartzo P7 | SI | 02SB | RF | P7Cav | - | GlassWinT | Mon | SI-02SB:RF-P7Cav:GlassWinT-Mon | SI-02SB:RF-P7Cav:GlassWinTUpperLimit-Cte | SI-02SB:RF-P7Cav:GlassWinTLowerLimit-Cte | SI_02SB_RF_P7Cav_GlassWinTMon | Analog | Input | Set_Temp[8] | Set_Temp[9] | C | SI_02SB_RF_P7Cav_GlassWinTMon | .5 | 2
46 | PT - 100 Janela de Quartzo P7 Abaixo do Set | SI | 02SB | RF | P7Cav | - | GlassWinTUp | Mon | SI-02SB:RF-P7Cav:GlassWinTUp-Mon | N/A | N/A | SI_02SB_RF_P7Cav_GlassWinTUpMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_GlassWinTUpMon | .1
47 | PT - 100 Janela de Quartzo P7 Acima do Set | SI | 02SB | RF | P7Cav | - | GlassWinTDown | Mon | SI-02SB:RF-P7Cav:GlassWinTDown-Mon | N/A | N/A | SI_02SB_RF_P7Cav_GlassWinTDownMon | Digital | Input | N/A | N/A |  | SI_02SB_RF_P7Cav_GlassWinTDownMon | .1
48 | Falha Skid Petra VII | UA |  | B19C20 | SkidP7 | - | OpIntlkRF | Mon | UA:B19C20SkidP7:OpIntlkRF-Mon | N/A | N/A | UA_B19C20_SkidP7_OpIntlkRFMon | Digital | Input |  |  |  | UA_B19C20_SkidP7_OpIntlkRFMon | .1
Note on A51: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Edição Manual nas colunas NAME e TAG - Provisório

## Interlock
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Sistema Anel A Interlock Sirius | RA | RaSIA02 | RF | IntlkCtrl | - | IntlkSirius | Mon | RA-RaSIA02:RF-IntlkCtrl:IntlkSirius-Mon | N/A | N/A | RA_RaSIA02_RF_IntlkCtrl_IntlkSiriusMon | Digital | Input |  |  |  | RA_RaSIA02_RF_IntlkCtrl_IntlkSiriusMon | .1
2 | Interlock para LLRF | RA | RaSIA02 | RF | IntlkCtrl | - | IntlkLLRF | Mon | RA-RaSIA02:RF-IntlkCtrl:IntlkLLRF-Mon | N/A | N/A | RA_RaSIA02_RF_IntlkCtrl_IntlkLLRFMon | Digital | Output |  |  |  | RA_RaSIA02_RF_IntlkCtrl_IntlkLLRFMon | .1
3 | Botão de emergencia do sistema de interlock | RA | RaSIA02 | RF | IntlkCtrl | - | EStop | Mon | RA-RaSIA02:RF-IntlkCtrl:EStop-Mon | N/A | N/A | RA_RaSIA02_RF_IntlkCtrl_EStopMon | Digital | Input |  |  |  | RA_RaSIA02_RF_IntlkCtrl_EStopMon | .1
4 | Reset de Falhas rack Interlock 02 | RA | RaSIA02 | RF | Intlk | - | Reset | Cmd | RA-RaSIA02:RF-Intlk:Reset-Cmd | N/A | N/A | RA_RaSIA02_RF_Intlk_ResetCmd | Digital | Control |  |  |  | RA_RaSIA02_RF_Intlk_ResetCmd | .1
5 | RF Operando para Interlock Sirius | SI | 02SB | RF | Intlk | - | RFOn | Mon | SI-02SB:RF-Intlk:RFOn-Mon | N/A | N/A | SI_02SB_RF_Intlk_RFOnMon | Digital | Output |  |  |  | SI_02SB_RF_Intlk_RFOnMon | .1
6 | Habilita Plungers | RA | RaSIA01 | RF | CavPlDrivers | - | DrEnbl | Sel | RA-RaSIA01:RF-CavPlDrivers:DrEnbl-Sel | N/A | N/A | RA_RaSIA01_RF_CavPlDrivers_DrEnblSel | Digital | Control |  |  |  | RA_RaSIA01_RF_CavPlDrivers_DrEnblSel | .1
7 | Readback Habilita Plungers | RA | RaSIA01 | RF | CavPlDrivers | - | DrEnbl | Sts | RA-RaSIA01:RF-CavPlDrivers:DrEnbl-Sts | N/A | N/A | RA_RaSIA01_RF_CavPlDrivers_DrEnblSts | Digital | Input |  |  |  | RA_RaSIA01_RF_CavPlDrivers_DrEnblSts | .1
8 | Fala geral hardware | RA | RaSIA02 | RF | Intlk | - | FaultHard | Mon | RA-RaSIA02:RF-Intlk:FaultHard-Mon | N/A | N/A | RA_RASIA02_RF_Intlk_FaultHardMon | Digital | Input |  |  |  | RA_RASIA02_RF_Intlk_FaultHardMon | .1
9 | Falha Remota 01 | RA | RaSIA02 | RF | IntlkComp | 1 | Op | Mon | RA-RaSIA02:RF-IntlkComp-1:Op-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OpMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OpMon | .1
10 | Falha Remota 02 | RA | RaSIA02 | RF | IntlkComp | 2 | Op | Mon | RA-RaSIA02:RF-IntlkComp-2:Op-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OpMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OpMon | .1
11 | Falha Hardware Cartão 01 Controladora | RA | RaSIA02 | RF | IntlkCtrl | - | IB1601Fault | Mon | RA-RaSIA02:RF-IntlkCtrl:IB1601Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IB1601FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IB1601FaultMon | .1
12 | Falha Hardware Cartão 02 Controladora | RA | RaSIA02 | RF | IntlkCtrl | - | IB1602Fault | Mon | RA-RaSIA02:RF-IntlkCtrl:IB1602Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IB1602FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IB1602FaultMon | .1
13 | Falha Hardware Cartão 03 Controladora | RA | RaSIA02 | RF | IntlkCtrl | - | IY403Fault | Mon | RA-RaSIA02:RF-IntlkCtrl:IY403Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IY403FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IY403FaultMon | .1
14 | Falha Hardware Cartão 04 Controladora | RA | RaSIA02 | RF | IntlkCtrl | - | IY404Fault | Mon | RA-RaSIA02:RF-IntlkCtrl:IY404Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IY404FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IY404FaultMon | .1
15 | Falha Hardware Cartão 05 Controladora | RA | RaSIA02 | RF | IntlkCtrl | - | IY405Fault | Mon | RA-RaSIA02:RF-IntlkCtrl:IY405Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IY405FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IY405FaultMon | .1
16 | Falha Hardware Cartão 06 Controladora | RA | RaSIA02 | RF | IntlkCtrl | - | OB1606Fault | Mon | RA-RaSIA02:RF-IntlkCtrl:OB1606Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OB1606FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OB1606FaultMon | .1
17 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 01 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig00 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig00Mon | .1
18 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 02 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig01 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig01Mon | .1
19 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 03 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig02 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig02Mon | .1
20 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 04 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig03 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig03Mon | .1
21 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 05 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig04 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig04Mon | .1
22 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 06 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig05 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig05Mon | .1
23 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 07 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig06 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig06Mon | .1
24 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 08 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig07 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig07Mon | .1
25 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 09 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig08 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig08Mon | .1
26 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 10 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig09 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig09Mon | .1
27 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 11 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig10 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig10Mon | .1
28 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 12 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig11 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig11Mon | .1
29 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 13 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig12 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig12Mon | .1
30 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 14 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig13 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig13Mon | .1
31 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 15 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig14 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig14Mon | .1
32 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 16 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig15 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig15Mon | .1
33 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 01 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig16 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig16Mon | .1
34 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 02 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig17 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig17Mon | .1
35 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 03 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig18 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig18Mon | .1
36 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 04 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig19 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig19Mon | .1
37 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 05 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig20 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig20-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig20Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig20Mon | .1
38 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 06 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig21 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig21-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig21Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig21Mon | .1
39 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 07 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig22 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig22-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig22Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig22Mon | .1
40 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 08 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig23 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig23-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig23Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig23Mon | .1
41 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 09 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig24 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig24-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig24Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig24Mon | .1
42 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 10 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig25 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig25-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig25Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig25Mon | .1
43 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 11 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig26 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig26-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig26Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig26Mon | .1
44 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 12 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig27 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig27-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig27Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig27Mon | .1
45 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 13 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig28 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig28-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig28Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig28Mon | .1
46 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 14 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig29 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig29-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig29Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig29Mon | .1
47 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 15 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig30 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig30-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig30Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig30Mon | .1
48 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 16 | RA | RaSIA02 | RF | IntlkCtrl | - | InDig31 | Mon | RA-RaSIA02:RF-IntlkCtrl:InDig31-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig31Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig31Mon | .1
49 | Falha Hardware Cartão 5069-IY4 03 Controladora Entrada 01 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng00 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng00Mon | .1
50 | Falha Hardware Cartão 5069-IY4 03 Controladora Entrada 02 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng01 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng01Mon | .1
51 | Falha Hardware Cartão 5069-IY4 03 Controladora Entrada 03 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng02 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng02Mon | .1
52 | Falha Hardware Cartão 5069-IY4 03 Controladora Entrada 04 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng03 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng03Mon | .1
53 | Falha Hardware Cartão 5069-IY4 04 Controladora Entrada 01 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng04 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng04Mon | .1
54 | Falha Hardware Cartão 5069-IY4 04 Controladora Entrada 02 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng05 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng05Mon | .1
55 | Falha Hardware Cartão 5069-IY4 04 Controladora Entrada 03 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng06 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng06Mon | .1
56 | Falha Hardware Cartão 5069-IY4 04 Controladora Entrada 04 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng07 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng07Mon | .1
57 | Falha Hardware Cartão 5069-IY4 05 Controladora Entrada 01 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng08 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng08Mon | .1
58 | Falha Hardware Cartão 5069-IY4 05 Controladora Entrada 02 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng09 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng09Mon | .1
59 | Falha Hardware Cartão 5069-IY4 05 Controladora Entrada 03 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng10 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng10Mon | .1
60 | Falha Hardware Cartão 5069-IY4 05 Controladora Entrada 04 | RA | RaSIA02 | RF | IntlkCtrl | - | InAng11 | Mon | RA-RaSIA02:RF-IntlkCtrl:InAng11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng11Mon | .1
61 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 01 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig00 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig00Mon | .1
62 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 02 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig01 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig01Mon | .1
63 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 03 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig02 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig02Mon | .1
64 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 04 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig03 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig03Mon | .1
65 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 05 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig04 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig04Mon | .1
66 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 06 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig05 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig05Mon | .1
67 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 07 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig06 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig06Mon | .1
68 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 08 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig07 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig07Mon | .1
69 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 09 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig08 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig08Mon | .1
70 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 10 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig09 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig09Mon | .1
71 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 11 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig10 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig10Mon | .1
72 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 12 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig11 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig11Mon | .1
73 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 13 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig12 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig12Mon | .1
74 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 14 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig13 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig13Mon | .1
75 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 15 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig14 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig14Mon | .1
76 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 16 | RA | RaSIA02 | RF | IntlkCtrl | - | OutDig15 | Mon | RA-RaSIA02:RF-IntlkCtrl:OutDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig15Mon | .1
77 | Falha Hardware Cartão 01 Remota 01 | RA | RaSIA02 | RF | IntlkComp | 1 | IB1601Fault | Mon | RA-RaSIA02:RF-IntlkComp-1:IB1601Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IB1601FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IB1601FaultMon | .1
78 | Falha Hardware Cartão 02 Remota 01 | RA | RaSIA02 | RF | IntlkComp | 1 | IB1602Fault | Mon | RA-RaSIA02:RF-IntlkComp-1:IB1602Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IB1602FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IB1602FaultMon | .1
79 | Falha Hardware Cartão 03 Remota 01 | RA | RaSIA02 | RF | IntlkComp | 1 | IY403Fault | Mon | RA-RaSIA02:RF-IntlkComp-1:IY403Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY403FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY403FaultMon | .1
80 | Falha Hardware Cartão 04 Remota 01 | RA | RaSIA02 | RF | IntlkComp | 1 | IY404Fault | Mon | RA-RaSIA02:RF-IntlkComp-1:IY404Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY404FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY404FaultMon | .1
81 | Falha Hardware Cartão 05 Remota 01 | RA | RaSIA02 | RF | IntlkComp | 1 | IY405Fault | Mon | RA-RaSIA02:RF-IntlkComp-1:IY405Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY405FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY405FaultMon | .1
82 | Falha Hardware Cartão 06 Remota 01 | RA | RaSIA02 | RF | IntlkComp | 1 | IY406Fault | Mon | RA-RaSIA02:RF-IntlkComp-1:IY406Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY406FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY406FaultMon | .1
83 | Falha Hardware Cartão 07 Remota 01 | RA | RaSIA02 | RF | IntlkComp | 1 | IY407Fault | Mon | RA-RaSIA02:RF-IntlkComp-1:IY407Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY407FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY407FaultMon | .1
84 | Falha Hardware Cartão 08 Remota 01 | RA | RaSIA02 | RF | IntlkComp | 1 | OB1608Fault | Mon | RA-RaSIA02:RF-IntlkComp-1:OB1608Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OB1608FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OB1608FaultMon | .1
85 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig00 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig00Mon | .1
86 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig01 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig01Mon | .1
87 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig02 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig02Mon | .1
88 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig03 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig03Mon | .1
89 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 05 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig04 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig04Mon | .1
90 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 06 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig05 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig05Mon | .1
91 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 07 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig06 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig06Mon | .1
92 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 08 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig07 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig07Mon | .1
93 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 09 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig08 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig08Mon | .1
94 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 10 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig09 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig09Mon | .1
95 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 11 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig10 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig10Mon | .1
96 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 12 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig11 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig11Mon | .1
97 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 13 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig12 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig12Mon | .1
98 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 14 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig13 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig13Mon | .1
99 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 15 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig14 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig14Mon | .1
100 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 16 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig15 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig15Mon | .1
101 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig16 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig16Mon | .1
102 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig17 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig17Mon | .1
103 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig18 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig18Mon | .1
104 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig19 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig19Mon | .1
105 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 05 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig20 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig20-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig20Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig20Mon | .1
106 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 06 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig21 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig21-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig21Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig21Mon | .1
107 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 07 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig22 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig22-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig22Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig22Mon | .1
108 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 08 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig23 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig23-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig23Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig23Mon | .1
109 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 09 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig24 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig24-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig24Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig24Mon | .1
110 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 10 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig25 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig25-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig25Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig25Mon | .1
111 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 11 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig26 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig26-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig26Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig26Mon | .1
112 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 12 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig27 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig27-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig27Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig27Mon | .1
113 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 13 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig28 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig28-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig28Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig28Mon | .1
114 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 14 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig29 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig29-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig29Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig29Mon | .1
115 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 15 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig30 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig30-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig30Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig30Mon | .1
116 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 16 | RA | RaSIA02 | RF | IntlkComp | 1 | InDig31 | Mon | RA-RaSIA02:RF-IntlkComp-1:InDig31-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig31Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig31Mon | .1
117 | Falha Hardware Cartão 5069-IY4 03 Remota 01 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng00 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng00Mon | .1
118 | Falha Hardware Cartão 5069-IY4 03 Remota 01 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng01 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng01Mon | .1
119 | Falha Hardware Cartão 5069-IY4 03 Remota 01 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng02 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng02Mon | .1
120 | Falha Hardware Cartão 5069-IY4 03 Remota 01 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng03 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng03Mon | .1
121 | Falha Hardware Cartão 5069-IY4 04 Remota 01 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng04 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng04Mon | .1
122 | Falha Hardware Cartão 5069-IY4 04 Remota 01 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng05 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng05Mon | .1
123 | Falha Hardware Cartão 5069-IY4 04 Remota 01 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng06 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng06Mon | .1
124 | Falha Hardware Cartão 5069-IY4 04 Remota 01 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng07 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng07Mon | .1
125 | Falha Hardware Cartão 5069-IY4 05 Remota 01 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng08 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng08Mon | .1
126 | Falha Hardware Cartão 5069-IY4 05 Remota 01 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng09 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng09Mon | .1
127 | Falha Hardware Cartão 5069-IY4 05 Remota 01 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng10 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng10Mon | .1
128 | Falha Hardware Cartão 5069-IY4 05 Remota 01 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng11 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng11Mon | .1
129 | Falha Hardware Cartão 5069-IY4 06 Remota 01 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng12 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng12Mon | .1
130 | Falha Hardware Cartão 5069-IY4 06 Remota 01 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng13 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng13Mon | .1
131 | Falha Hardware Cartão 5069-IY4 06 Remota 01 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng14 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng14Mon | .1
132 | Falha Hardware Cartão 5069-IY4 06 Remota 01 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng15 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng15Mon | .1
133 | Falha Hardware Cartão 5069-IY4 07 Remota 01 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng16 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng16Mon | .1
134 | Falha Hardware Cartão 5069-IY4 07 Remota 01 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng17 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng17Mon | .1
135 | Falha Hardware Cartão 5069-IY4 07 Remota 01 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng18 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng18Mon | .1
136 | Falha Hardware Cartão 5069-IY4 07 Remota 01 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 1 | InAng19 | Mon | RA-RaSIA02:RF-IntlkComp-1:InAng19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng19Mon | .1
137 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 01 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig00 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig00Mon | .1
138 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 02 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig01 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig01Mon | .1
139 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 03 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig02 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig02Mon | .1
140 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 04 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig03 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig03Mon | .1
141 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 05 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig04 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig04Mon | .1
142 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 06 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig05 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig05Mon | .1
143 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 07 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig06 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig06Mon | .1
144 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 08 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig07 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig07Mon | .1
145 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 09 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig08 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig08Mon | .1
146 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 10 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig09 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig09Mon | .1
147 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 11 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig10 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig10Mon | .1
148 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 12 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig11 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig11Mon | .1
149 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 13 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig12 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig12Mon | .1
150 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 14 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig13 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig13Mon | .1
151 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 15 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig14 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig14Mon | .1
152 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 16 | RA | RaSIA02 | RF | IntlkComp | 1 | OutDig15 | Mon | RA-RaSIA02:RF-IntlkComp-1:OutDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig15Mon | .1
153 | Falha Hardware Cartão 01 Remota 02 | RA | RaSIA02 | RF | IntlkComp | 2 | IB1601Fault | Mon | RA-RaSIA02:RF-IntlkComp-2:IB1601Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IB1601FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IB1601FaultMon | .1
154 | Falha Hardware Cartão 02 Remota 02 | RA | RaSIA02 | RF | IntlkComp | 2 | IB1602Fault | Mon | RA-RaSIA02:RF-IntlkComp-2:IB1602Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IB1602FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IB1602FaultMon | .1
155 | Falha Hardware Cartão 03 Remota 02 | RA | RaSIA02 | RF | IntlkComp | 2 | IY403Fault | Mon | RA-RaSIA02:RF-IntlkComp-2:IY403Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY403FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY403FaultMon | .1
156 | Falha Hardware Cartão 04 Remota 02 | RA | RaSIA02 | RF | IntlkComp | 2 | IY404Fault | Mon | RA-RaSIA02:RF-IntlkComp-2:IY404Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY404FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY404FaultMon | .1
157 | Falha Hardware Cartão 05 Remota 02 | RA | RaSIA02 | RF | IntlkComp | 2 | IY405Fault | Mon | RA-RaSIA02:RF-IntlkComp-2:IY405Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY405FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY405FaultMon | .1
158 | Falha Hardware Cartão 06 Remota 02 | RA | RaSIA02 | RF | IntlkComp | 2 | IY406Fault | Mon | RA-RaSIA02:RF-IntlkComp-2:IY406Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY406FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY406FaultMon | .1
159 | Falha Hardware Cartão 07 Remota 02 | RA | RaSIA02 | RF | IntlkComp | 2 | IY407Fault | Mon | RA-RaSIA02:RF-IntlkComp-2:IY407Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY407FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY407FaultMon | .1
160 | Falha Hardware Cartão 08 Remota 02 | RA | RaSIA02 | RF | IntlkComp | 2 | OB1608Fault | Mon | RA-RaSIA02:RF-IntlkComp-2:OB1608Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OB1608FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OB1608FaultMon | .1
161 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig00 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig00Mon | .1
162 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig01 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig01Mon | .1
163 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig02 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig02Mon | .1
164 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig03 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig03Mon | .1
165 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 05 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig04 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig04Mon | .1
166 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 06 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig05 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig05Mon | .1
167 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 07 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig06 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig06Mon | .1
168 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 08 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig07 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig07Mon | .1
169 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 09 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig08 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig08Mon | .1
170 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 10 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig09 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig09Mon | .1
171 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 11 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig10 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig10Mon | .1
172 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 12 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig11 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig11Mon | .1
173 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 13 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig12 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig12Mon | .1
174 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 14 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig13 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig13Mon | .1
175 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 15 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig14 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig14Mon | .1
176 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 16 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig15 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig15Mon | .1
177 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig16 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig16Mon | .1
178 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig17 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig17Mon | .1
179 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig18 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig18Mon | .1
180 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig19 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig19Mon | .1
181 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 05 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig20 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig20-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig20Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig20Mon | .1
182 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 06 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig21 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig21-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig21Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig21Mon | .1
183 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 07 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig22 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig22-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig22Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig22Mon | .1
184 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 08 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig23 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig23-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig23Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig23Mon | .1
185 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 09 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig24 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig24-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig24Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig24Mon | .1
186 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 10 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig25 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig25-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig25Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig25Mon | .1
187 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 11 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig26 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig26-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig26Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig26Mon | .1
188 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 12 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig27 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig27-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig27Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig27Mon | .1
189 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 13 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig28 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig28-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig28Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig28Mon | .1
190 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 14 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig29 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig29-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig29Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig29Mon | .1
191 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 15 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig30 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig30-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig30Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig30Mon | .1
192 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 16 | RA | RaSIA02 | RF | IntlkComp | 2 | InDig31 | Mon | RA-RaSIA02:RF-IntlkComp-2:InDig31-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig31Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig31Mon | .1
193 | Falha Hardware Cartão 5069-IY4 03 Remota 02 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng00 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng00Mon | .1
194 | Falha Hardware Cartão 5069-IY4 03 Remota 02 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng01 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng01Mon | .1
195 | Falha Hardware Cartão 5069-IY4 03 Remota 02 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng02 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng02Mon | .1
196 | Falha Hardware Cartão 5069-IY4 03 Remota 02 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng03 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng03Mon | .1
197 | Falha Hardware Cartão 5069-IY4 04 Remota 02 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng04 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng04Mon | .1
198 | Falha Hardware Cartão 5069-IY4 04 Remota 02 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng05 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng05Mon | .1
199 | Falha Hardware Cartão 5069-IY4 04 Remota 02 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng06 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng06Mon | .1
200 | Falha Hardware Cartão 5069-IY4 04 Remota 02 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng07 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng07Mon | .1
201 | Falha Hardware Cartão 5069-IY4 05 Remota 02 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng08 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng08Mon | .1
202 | Falha Hardware Cartão 5069-IY4 05 Remota 02 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng09 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng09Mon | .1
203 | Falha Hardware Cartão 5069-IY4 05 Remota 02 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng10 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng10Mon | .1
204 | Falha Hardware Cartão 5069-IY4 05 Remota 02 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng11 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng11Mon | .1
205 | Falha Hardware Cartão 5069-IY4 06 Remota 02 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng12 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng12Mon | .1
206 | Falha Hardware Cartão 5069-IY4 06 Remota 02 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng13 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng13Mon | .1
207 | Falha Hardware Cartão 5069-IY4 06 Remota 02 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng14 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng14Mon | .1
208 | Falha Hardware Cartão 5069-IY4 06 Remota 02 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng15 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng15Mon | .1
209 | Falha Hardware Cartão 5069-IY4 07 Remota 02 Entrada 01 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng16 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng16Mon | .1
210 | Falha Hardware Cartão 5069-IY4 07 Remota 02 Entrada 02 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng17 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng17Mon | .1
211 | Falha Hardware Cartão 5069-IY4 07 Remota 02 Entrada 03 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng18 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng18Mon | .1
212 | Falha Hardware Cartão 5069-IY4 07 Remota 02 Entrada 04 | RA | RaSIA02 | RF | IntlkComp | 2 | InAng19 | Mon | RA-RaSIA02:RF-IntlkComp-2:InAng19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng19Mon | .1
213 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 01 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig00 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig00Mon | .1
214 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 02 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig01 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig01Mon | .1
215 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 03 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig02 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig02Mon | .1
216 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 04 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig03 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig03Mon | .1
217 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 05 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig04 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig04Mon | .1
218 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 06 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig05 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig05Mon | .1
219 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 07 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig06 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig06Mon | .1
220 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 08 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig07 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig07Mon | .1
221 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 09 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig08 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig08Mon | .1
222 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 10 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig09 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig09Mon | .1
223 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 11 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig10 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig10Mon | .1
224 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 12 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig11 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig11Mon | .1
225 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 13 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig12 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig12Mon | .1
226 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 14 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig13 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig13Mon | .1
227 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 15 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig14 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig14Mon | .1
228 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 16 | RA | RaSIA02 | RF | IntlkComp | 2 | OutDig15 | Mon | RA-RaSIA02:RF-IntlkComp-2:OutDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig15Mon | .1

## Interlock_B
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec | Cmd Duration | PV Conversion | Upper Limit Conversion | Lower Limit Conversion
1 | Reset de Falhas Rack Interlock Sistema Anel B | RA | RaSIB02 | RF | Intlk | - | Reset | Cmd | RA-RaSIB02:RF-Intlk:Reset-Cmd | N/A | N/A | Memorias[19].15 | Digital | Control |  |  |  | Memorias[19].15 | .1 |  | 0.5

## Interlock_B_future
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Sistema Anel B Interlock Sirius | RA | RaSIB02 | RF | IntlkCtrl | - | IntlkSirius | Mon | RA-RaSIB02:RF-IntlkCtrl:IntlkSirius-Mon | N/A | N/A | RA_RaSIB02_RF_IntlkCtrl_IntlkSiriusMon | Digital | Input |  |  |  | RA_RaSIB02_RF_IntlkCtrl_IntlkSiriusMon | .1
2 | Interlock para LLRF | RA | RaSIB02 | RF | IntlkCtrl | - | IntlkLLRF | Mon | RA-RaSIB02:RF-IntlkCtrl:IntlkLLRF-Mon | N/A | N/A | RA_RaSIB02_RF_IntlkCtrl_IntlkLLRFMon | Digital | Output |  |  |  | RA_RaSIB02_RF_IntlkCtrl_IntlkLLRFMon | .1
3 | Botão de emergencia do sistema de interlock | RA | RaSIB02 | RF | IntlkCtrl | - | EStop | Mon | RA-RaSIB02:RF-IntlkCtrl:EStop-Mon | N/A | N/A | RA_RaSIB02_RF_IntlkCtrl_EStopMon | Digital | Input |  |  |  | RA_RaSIB02_RF_IntlkCtrl_EStopMon | .1
4 | Reset de Falhas Rack Interlock | RA | RaSIB02 | RF | Intlk | - | Reset | Cmd | RA-RaSIB02:RF-Intlk:Reset-Cmd | N/A | N/A | RA_RaSIB02_RF_Intlk_ResetCmd | Digital | Control |  |  |  | RA_RaSIB02_RF_Intlk_ResetCmd | .1
5 | RF Operando para Interlock Sirius | SI | 03SB | RF | Intlk | - | RFOn | Mon | SI-03SB:RF-Intlk:RFOn-Mon | N/A | N/A | SI_03SB_RF_Intlk_RFOnMon | Digital | Output |  |  |  | SI_03SB_RF_Intlk_RFOnMon | .1
6 | Habilita Plungers | RA | RaSIB01 | RF | CavPlDrivers | - | DrEnbl | Sel | RA-RaSIB01:RF-CavPlDrivers:DrEnbl-Sel | N/A | N/A | RA_RaSIB01_RF_CavPlDrivers_DrEnblSel | Digital | Control |  |  |  | RA_RaSIB01_RF_CavPlDrivers_DrEnblSel | .1
7 | Readback Habilita Plungers | RA | RaSIB01 | RF | CavPlDrivers | - | DrEnbl | Sts | RA-RaSIB01:RF-CavPlDrivers:DrEnbl-Sts | N/A | N/A | RA_RaSIB01_RF_CavPlDrivers_DrEnblSts | Digital | Input |  |  |  | RA_RaSIB01_RF_CavPlDrivers_DrEnblSts | .1
8 | Fala geral hardware | RA | RaSIB02 | RF | Intlk | - | FaultHard | Mon | RA-RaSIB02:RF-Intlk:FaultHard-Mon | N/A | N/A | RA_RASIA02_RF_Intlk_FaultHardMon | Digital | Input |  |  |  | RA_RASIA02_RF_Intlk_FaultHardMon | .1
9 | Falha Remota 01 | RA | RaSIB02 | RF | IntlkComp | 1 | Op | Mon | RA-RaSIB02:RF-IntlkComp-1:Op-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OpMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OpMon | .1
10 | Falha Remota 02 | RA | RaSIB02 | RF | IntlkComp | 2 | Op | Mon | RA-RaSIB02:RF-IntlkComp-2:Op-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OpMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OpMon | .1
11 | Falha Hardware Cartão 01 Controladora | RA | RaSIB02 | RF | IntlkCtrl | - | IB1601Fault | Mon | RA-RaSIB02:RF-IntlkCtrl:IB1601Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IB1601FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IB1601FaultMon | .1
12 | Falha Hardware Cartão 02 Controladora | RA | RaSIB02 | RF | IntlkCtrl | - | IB1602Fault | Mon | RA-RaSIB02:RF-IntlkCtrl:IB1602Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IB1602FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IB1602FaultMon | .1
13 | Falha Hardware Cartão 03 Controladora | RA | RaSIB02 | RF | IntlkCtrl | - | IY403Fault | Mon | RA-RaSIB02:RF-IntlkCtrl:IY403Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IY403FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IY403FaultMon | .1
14 | Falha Hardware Cartão 04 Controladora | RA | RaSIB02 | RF | IntlkCtrl | - | IY404Fault | Mon | RA-RaSIB02:RF-IntlkCtrl:IY404Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IY404FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IY404FaultMon | .1
15 | Falha Hardware Cartão 05 Controladora | RA | RaSIB02 | RF | IntlkCtrl | - | IY405Fault | Mon | RA-RaSIB02:RF-IntlkCtrl:IY405Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_IY405FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_IY405FaultMon | .1
16 | Falha Hardware Cartão 06 Controladora | RA | RaSIB02 | RF | IntlkCtrl | - | OB1606Fault | Mon | RA-RaSIB02:RF-IntlkCtrl:OB1606Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OB1606FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OB1606FaultMon | .1
17 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 01 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig00 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig00Mon | .1
18 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 02 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig01 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig01Mon | .1
19 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 03 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig02 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig02Mon | .1
20 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 04 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig03 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig03Mon | .1
21 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 05 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig04 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig04Mon | .1
22 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 06 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig05 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig05Mon | .1
23 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 07 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig06 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig06Mon | .1
24 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 08 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig07 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig07Mon | .1
25 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 09 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig08 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig08Mon | .1
26 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 10 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig09 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig09Mon | .1
27 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 11 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig10 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig10Mon | .1
28 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 12 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig11 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig11Mon | .1
29 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 13 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig12 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig12Mon | .1
30 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 14 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig13 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig13Mon | .1
31 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 15 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig14 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig14Mon | .1
32 | Falha Hardware Cartão 5069-IB16 01 Controladora Entrada 16 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig15 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig15Mon | .1
33 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 01 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig16 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig16Mon | .1
34 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 02 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig17 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig17Mon | .1
35 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 03 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig18 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig18Mon | .1
36 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 04 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig19 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig19Mon | .1
37 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 05 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig20 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig20-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig20Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig20Mon | .1
38 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 06 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig21 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig21-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig21Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig21Mon | .1
39 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 07 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig22 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig22-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig22Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig22Mon | .1
40 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 08 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig23 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig23-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig23Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig23Mon | .1
41 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 09 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig24 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig24-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig24Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig24Mon | .1
42 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 10 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig25 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig25-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig25Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig25Mon | .1
43 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 11 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig26 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig26-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig26Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig26Mon | .1
44 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 12 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig27 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig27-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig27Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig27Mon | .1
45 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 13 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig28 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig28-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig28Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig28Mon | .1
46 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 14 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig29 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig29-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig29Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig29Mon | .1
47 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 15 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig30 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig30-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig30Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig30Mon | .1
48 | Falha Hardware Cartão 5069-IB16 02 Controladora Entrada 16 | RA | RaSIB02 | RF | IntlkCtrl | - | InDig31 | Mon | RA-RaSIB02:RF-IntlkCtrl:InDig31-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InDig31Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InDig31Mon | .1
49 | Falha Hardware Cartão 5069-IY4 03 Controladora Entrada 01 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng00 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng00Mon | .1
50 | Falha Hardware Cartão 5069-IY4 03 Controladora Entrada 02 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng01 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng01Mon | .1
51 | Falha Hardware Cartão 5069-IY4 03 Controladora Entrada 03 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng02 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng02Mon | .1
52 | Falha Hardware Cartão 5069-IY4 03 Controladora Entrada 04 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng03 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng03Mon | .1
53 | Falha Hardware Cartão 5069-IY4 04 Controladora Entrada 01 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng04 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng04Mon | .1
54 | Falha Hardware Cartão 5069-IY4 04 Controladora Entrada 02 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng05 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng05Mon | .1
55 | Falha Hardware Cartão 5069-IY4 04 Controladora Entrada 03 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng06 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng06Mon | .1
56 | Falha Hardware Cartão 5069-IY4 04 Controladora Entrada 04 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng07 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng07Mon | .1
57 | Falha Hardware Cartão 5069-IY4 05 Controladora Entrada 01 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng08 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng08Mon | .1
58 | Falha Hardware Cartão 5069-IY4 05 Controladora Entrada 02 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng09 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng09Mon | .1
59 | Falha Hardware Cartão 5069-IY4 05 Controladora Entrada 03 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng10 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng10Mon | .1
60 | Falha Hardware Cartão 5069-IY4 05 Controladora Entrada 04 | RA | RaSIB02 | RF | IntlkCtrl | - | InAng11 | Mon | RA-RaSIB02:RF-IntlkCtrl:InAng11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_InAng11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_InAng11Mon | .1
61 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 01 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig00 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig00Mon | .1
62 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 02 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig01 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig01Mon | .1
63 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 03 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig02 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig02Mon | .1
64 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 04 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig03 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig03Mon | .1
65 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 05 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig04 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig04Mon | .1
66 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 06 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig05 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig05Mon | .1
67 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 07 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig06 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig06Mon | .1
68 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 08 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig07 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig07Mon | .1
69 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 09 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig08 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig08Mon | .1
70 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 10 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig09 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig09Mon | .1
71 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 11 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig10 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig10Mon | .1
72 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 12 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig11 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig11Mon | .1
73 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 13 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig12 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig12Mon | .1
74 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 14 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig13 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig13Mon | .1
75 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 15 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig14 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig14Mon | .1
76 | Falha Hardware Cartão 5069-OB16 06 Controladora Saída 16 | RA | RaSIB02 | RF | IntlkCtrl | - | OutDig15 | Mon | RA-RaSIB02:RF-IntlkCtrl:OutDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkCtrl_OutDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkCtrl_OutDig15Mon | .1
77 | Falha Hardware Cartão 01 Remota 01 | RA | RaSIB02 | RF | IntlkComp | 1 | IB1601Fault | Mon | RA-RaSIB02:RF-IntlkComp-1:IB1601Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IB1601FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IB1601FaultMon | .1
78 | Falha Hardware Cartão 02 Remota 01 | RA | RaSIB02 | RF | IntlkComp | 1 | IB1602Fault | Mon | RA-RaSIB02:RF-IntlkComp-1:IB1602Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IB1602FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IB1602FaultMon | .1
79 | Falha Hardware Cartão 03 Remota 01 | RA | RaSIB02 | RF | IntlkComp | 1 | IY403Fault | Mon | RA-RaSIB02:RF-IntlkComp-1:IY403Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY403FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY403FaultMon | .1
80 | Falha Hardware Cartão 04 Remota 01 | RA | RaSIB02 | RF | IntlkComp | 1 | IY404Fault | Mon | RA-RaSIB02:RF-IntlkComp-1:IY404Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY404FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY404FaultMon | .1
81 | Falha Hardware Cartão 05 Remota 01 | RA | RaSIB02 | RF | IntlkComp | 1 | IY405Fault | Mon | RA-RaSIB02:RF-IntlkComp-1:IY405Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY405FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY405FaultMon | .1
82 | Falha Hardware Cartão 06 Remota 01 | RA | RaSIB02 | RF | IntlkComp | 1 | IY406Fault | Mon | RA-RaSIB02:RF-IntlkComp-1:IY406Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY406FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY406FaultMon | .1
83 | Falha Hardware Cartão 07 Remota 01 | RA | RaSIB02 | RF | IntlkComp | 1 | IY407Fault | Mon | RA-RaSIB02:RF-IntlkComp-1:IY407Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_IY407FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_IY407FaultMon | .1
84 | Falha Hardware Cartão 08 Remota 01 | RA | RaSIB02 | RF | IntlkComp | 1 | OB1608Fault | Mon | RA-RaSIB02:RF-IntlkComp-1:OB1608Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OB1608FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OB1608FaultMon | .1
85 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig00 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig00Mon | .1
86 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig01 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig01Mon | .1
87 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig02 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig02Mon | .1
88 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig03 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig03Mon | .1
89 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 05 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig04 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig04Mon | .1
90 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 06 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig05 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig05Mon | .1
91 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 07 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig06 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig06Mon | .1
92 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 08 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig07 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig07Mon | .1
93 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 09 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig08 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig08Mon | .1
94 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 10 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig09 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig09Mon | .1
95 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 11 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig10 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig10Mon | .1
96 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 12 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig11 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig11Mon | .1
97 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 13 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig12 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig12Mon | .1
98 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 14 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig13 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig13Mon | .1
99 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 15 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig14 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig14Mon | .1
100 | Falha Hardware Cartão 5069-IB16 01 Remota 01 Entrada 16 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig15 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig15Mon | .1
101 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig16 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig16Mon | .1
102 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig17 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig17Mon | .1
103 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig18 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig18Mon | .1
104 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig19 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig19Mon | .1
105 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 05 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig20 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig20-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig20Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig20Mon | .1
106 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 06 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig21 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig21-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig21Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig21Mon | .1
107 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 07 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig22 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig22-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig22Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig22Mon | .1
108 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 08 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig23 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig23-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig23Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig23Mon | .1
109 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 09 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig24 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig24-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig24Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig24Mon | .1
110 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 10 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig25 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig25-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig25Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig25Mon | .1
111 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 11 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig26 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig26-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig26Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig26Mon | .1
112 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 12 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig27 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig27-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig27Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig27Mon | .1
113 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 13 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig28 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig28-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig28Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig28Mon | .1
114 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 14 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig29 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig29-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig29Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig29Mon | .1
115 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 15 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig30 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig30-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig30Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig30Mon | .1
116 | Falha Hardware Cartão 5069-IB16 02 Remota 01 Entrada 16 | RA | RaSIB02 | RF | IntlkComp | 1 | InDig31 | Mon | RA-RaSIB02:RF-IntlkComp-1:InDig31-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InDig31Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InDig31Mon | .1
117 | Falha Hardware Cartão 5069-IY4 03 Remota 01 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng00 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng00Mon | .1
118 | Falha Hardware Cartão 5069-IY4 03 Remota 01 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng01 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng01Mon | .1
119 | Falha Hardware Cartão 5069-IY4 03 Remota 01 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng02 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng02Mon | .1
120 | Falha Hardware Cartão 5069-IY4 03 Remota 01 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng03 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng03Mon | .1
121 | Falha Hardware Cartão 5069-IY4 04 Remota 01 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng04 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng04Mon | .1
122 | Falha Hardware Cartão 5069-IY4 04 Remota 01 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng05 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng05Mon | .1
123 | Falha Hardware Cartão 5069-IY4 04 Remota 01 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng06 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng06Mon | .1
124 | Falha Hardware Cartão 5069-IY4 04 Remota 01 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng07 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng07Mon | .1
125 | Falha Hardware Cartão 5069-IY4 05 Remota 01 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng08 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng08Mon | .1
126 | Falha Hardware Cartão 5069-IY4 05 Remota 01 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng09 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng09Mon | .1
127 | Falha Hardware Cartão 5069-IY4 05 Remota 01 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng10 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng10Mon | .1
128 | Falha Hardware Cartão 5069-IY4 05 Remota 01 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng11 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng11Mon | .1
129 | Falha Hardware Cartão 5069-IY4 06 Remota 01 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng12 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng12Mon | .1
130 | Falha Hardware Cartão 5069-IY4 06 Remota 01 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng13 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng13Mon | .1
131 | Falha Hardware Cartão 5069-IY4 06 Remota 01 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng14 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng14Mon | .1
132 | Falha Hardware Cartão 5069-IY4 06 Remota 01 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng15 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng15Mon | .1
133 | Falha Hardware Cartão 5069-IY4 07 Remota 01 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng16 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng16Mon | .1
134 | Falha Hardware Cartão 5069-IY4 07 Remota 01 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng17 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng17Mon | .1
135 | Falha Hardware Cartão 5069-IY4 07 Remota 01 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng18 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng18Mon | .1
136 | Falha Hardware Cartão 5069-IY4 07 Remota 01 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 1 | InAng19 | Mon | RA-RaSIB02:RF-IntlkComp-1:InAng19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_InAng19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_InAng19Mon | .1
137 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 01 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig00 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig00Mon | .1
138 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 02 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig01 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig01Mon | .1
139 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 03 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig02 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig02Mon | .1
140 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 04 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig03 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig03Mon | .1
141 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 05 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig04 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig04Mon | .1
142 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 06 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig05 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig05Mon | .1
143 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 07 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig06 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig06Mon | .1
144 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 08 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig07 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig07Mon | .1
145 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 09 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig08 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig08Mon | .1
146 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 10 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig09 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig09Mon | .1
147 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 11 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig10 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig10Mon | .1
148 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 12 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig11 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig11Mon | .1
149 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 13 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig12 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig12Mon | .1
150 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 14 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig13 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig13Mon | .1
151 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 15 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig14 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig14Mon | .1
152 | Falha Hardware Cartão 5069-OB16 08 Remota 01 Saída 16 | RA | RaSIB02 | RF | IntlkComp | 1 | OutDig15 | Mon | RA-RaSIB02:RF-IntlkComp-1:OutDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_1_OutDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_1_OutDig15Mon | .1
153 | Falha Hardware Cartão 01 Remota 02 | RA | RaSIB02 | RF | IntlkComp | 2 | IB1601Fault | Mon | RA-RaSIB02:RF-IntlkComp-2:IB1601Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IB1601FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IB1601FaultMon | .1
154 | Falha Hardware Cartão 02 Remota 02 | RA | RaSIB02 | RF | IntlkComp | 2 | IB1602Fault | Mon | RA-RaSIB02:RF-IntlkComp-2:IB1602Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IB1602FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IB1602FaultMon | .1
155 | Falha Hardware Cartão 03 Remota 02 | RA | RaSIB02 | RF | IntlkComp | 2 | IY403Fault | Mon | RA-RaSIB02:RF-IntlkComp-2:IY403Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY403FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY403FaultMon | .1
156 | Falha Hardware Cartão 04 Remota 02 | RA | RaSIB02 | RF | IntlkComp | 2 | IY404Fault | Mon | RA-RaSIB02:RF-IntlkComp-2:IY404Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY404FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY404FaultMon | .1
157 | Falha Hardware Cartão 05 Remota 02 | RA | RaSIB02 | RF | IntlkComp | 2 | IY405Fault | Mon | RA-RaSIB02:RF-IntlkComp-2:IY405Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY405FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY405FaultMon | .1
158 | Falha Hardware Cartão 06 Remota 02 | RA | RaSIB02 | RF | IntlkComp | 2 | IY406Fault | Mon | RA-RaSIB02:RF-IntlkComp-2:IY406Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY406FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY406FaultMon | .1
159 | Falha Hardware Cartão 07 Remota 02 | RA | RaSIB02 | RF | IntlkComp | 2 | IY407Fault | Mon | RA-RaSIB02:RF-IntlkComp-2:IY407Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_IY407FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_IY407FaultMon | .1
160 | Falha Hardware Cartão 08 Remota 02 | RA | RaSIB02 | RF | IntlkComp | 2 | OB1608Fault | Mon | RA-RaSIB02:RF-IntlkComp-2:OB1608Fault-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OB1608FaultMon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OB1608FaultMon | .1
161 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig00 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig00Mon | .1
162 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig01 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig01Mon | .1
163 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig02 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig02Mon | .1
164 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig03 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig03Mon | .1
165 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 05 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig04 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig04Mon | .1
166 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 06 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig05 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig05Mon | .1
167 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 07 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig06 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig06Mon | .1
168 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 08 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig07 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig07Mon | .1
169 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 09 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig08 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig08Mon | .1
170 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 10 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig09 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig09Mon | .1
171 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 11 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig10 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig10Mon | .1
172 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 12 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig11 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig11Mon | .1
173 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 13 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig12 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig12Mon | .1
174 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 14 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig13 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig13Mon | .1
175 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 15 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig14 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig14Mon | .1
176 | Falha Hardware Cartão 5069-IB16 01 Remota 02 Entrada 16 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig15 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig15Mon | .1
177 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig16 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig16Mon | .1
178 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig17 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig17Mon | .1
179 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig18 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig18Mon | .1
180 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig19 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig19Mon | .1
181 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 05 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig20 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig20-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig20Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig20Mon | .1
182 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 06 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig21 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig21-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig21Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig21Mon | .1
183 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 07 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig22 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig22-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig22Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig22Mon | .1
184 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 08 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig23 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig23-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig23Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig23Mon | .1
185 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 09 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig24 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig24-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig24Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig24Mon | .1
186 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 10 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig25 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig25-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig25Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig25Mon | .1
187 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 11 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig26 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig26-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig26Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig26Mon | .1
188 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 12 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig27 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig27-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig27Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig27Mon | .1
189 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 13 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig28 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig28-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig28Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig28Mon | .1
190 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 14 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig29 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig29-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig29Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig29Mon | .1
191 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 15 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig30 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig30-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig30Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig30Mon | .1
192 | Falha Hardware Cartão 5069-IB16 02 Remota 02 Entrada 16 | RA | RaSIB02 | RF | IntlkComp | 2 | InDig31 | Mon | RA-RaSIB02:RF-IntlkComp-2:InDig31-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InDig31Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InDig31Mon | .1
193 | Falha Hardware Cartão 5069-IY4 03 Remota 02 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng00 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng00Mon | .1
194 | Falha Hardware Cartão 5069-IY4 03 Remota 02 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng01 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng01Mon | .1
195 | Falha Hardware Cartão 5069-IY4 03 Remota 02 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng02 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng02Mon | .1
196 | Falha Hardware Cartão 5069-IY4 03 Remota 02 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng03 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng03Mon | .1
197 | Falha Hardware Cartão 5069-IY4 04 Remota 02 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng04 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng04Mon | .1
198 | Falha Hardware Cartão 5069-IY4 04 Remota 02 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng05 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng05Mon | .1
199 | Falha Hardware Cartão 5069-IY4 04 Remota 02 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng06 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng06Mon | .1
200 | Falha Hardware Cartão 5069-IY4 04 Remota 02 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng07 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng07Mon | .1
201 | Falha Hardware Cartão 5069-IY4 05 Remota 02 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng08 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng08Mon | .1
202 | Falha Hardware Cartão 5069-IY4 05 Remota 02 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng09 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng09Mon | .1
203 | Falha Hardware Cartão 5069-IY4 05 Remota 02 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng10 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng10Mon | .1
204 | Falha Hardware Cartão 5069-IY4 05 Remota 02 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng11 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng11Mon | .1
205 | Falha Hardware Cartão 5069-IY4 06 Remota 02 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng12 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng12Mon | .1
206 | Falha Hardware Cartão 5069-IY4 06 Remota 02 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng13 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng13Mon | .1
207 | Falha Hardware Cartão 5069-IY4 06 Remota 02 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng14 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng14Mon | .1
208 | Falha Hardware Cartão 5069-IY4 06 Remota 02 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng15 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng15Mon | .1
209 | Falha Hardware Cartão 5069-IY4 07 Remota 02 Entrada 01 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng16 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng16-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng16Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng16Mon | .1
210 | Falha Hardware Cartão 5069-IY4 07 Remota 02 Entrada 02 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng17 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng17-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng17Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng17Mon | .1
211 | Falha Hardware Cartão 5069-IY4 07 Remota 02 Entrada 03 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng18 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng18-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng18Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng18Mon | .1
212 | Falha Hardware Cartão 5069-IY4 07 Remota 02 Entrada 04 | RA | RaSIB02 | RF | IntlkComp | 2 | InAng19 | Mon | RA-RaSIB02:RF-IntlkComp-2:InAng19-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_InAng19Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_InAng19Mon | .1
213 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 01 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig00 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig00-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig00Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig00Mon | .1
214 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 02 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig01 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig01-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig01Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig01Mon | .1
215 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 03 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig02 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig02-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig02Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig02Mon | .1
216 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 04 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig03 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig03-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig03Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig03Mon | .1
217 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 05 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig04 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig04-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig04Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig04Mon | .1
218 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 06 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig05 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig05-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig05Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig05Mon | .1
219 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 07 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig06 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig06-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig06Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig06Mon | .1
220 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 08 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig07 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig07-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig07Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig07Mon | .1
221 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 09 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig08 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig08-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig08Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig08Mon | .1
222 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 10 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig09 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig09-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig09Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig09Mon | .1
223 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 11 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig10 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig10-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig10Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig10Mon | .1
224 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 12 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig11 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig11-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig11Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig11Mon | .1
225 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 13 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig12 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig12-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig12Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig12Mon | .1
226 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 14 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig13 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig13-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig13Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig13Mon | .1
227 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 15 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig14 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig14-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig14Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig14Mon | .1
228 | Falha Hardware Cartão 5069-OB16 08 Remota 02 Saída 16 | RA | RaSIB02 | RF | IntlkComp | 2 | OutDig15 | Mon | RA-RaSIB02:RF-IntlkComp-2:OutDig15-Mon | N/A | N/A | RA_RASIA02_RF_IntlkComp_2_OutDig15Mon | Digital | Input |  |  |  | RA_RASIA02_RF_IntlkComp_2_OutDig15Mon | .1

## Petra 7 WaterTemp
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Disc 1 Water Temperature | SI | 02SB | RF | P7Cav | - | Disc1WT | Mon | SI-02SB:RF-P7Cav:Disc1WT-Mon | [9 empty] | 0.5
2 | Disc 2 Water Temperature | SI | 02SB | RF | P7Cav | - | Disc2WT | Mon | SI-02SB:RF-P7Cav:Disc2WT-Mon | [9 empty] | 0.5
3 | Cell 1 Water Temperature | SI | 02SB | RF | P7Cav | - | Cylin1WT | Mon | SI-02SB:RF-P7Cav:Cylin1WT-Mon | [9 empty] | 0.5
4 | Plunger 2 Water Temperature | SI | 02SB | RF | P7Cav | - | Pl2WT | Mon | SI-02SB:RF-P7Cav:Pl2WT-Mon | [9 empty] | 0.5
5 | Disc 3 Water Temperature | SI | 02SB | RF | P7Cav | - | Disc3WT | Mon | SI-02SB:RF-P7Cav:Disc3WT-Mon | [9 empty] | 0.5
6 | Cell 2 Water Temperature | SI | 02SB | RF | P7Cav | - | Cylin2WT | Mon | SI-02SB:RF-P7Cav:Cylin2WT-Mon | [9 empty] | 0.5
7 | Cell 3 Water Temperature | SI | 02SB | RF | P7Cav | - | Cylin3WT | Mon | SI-02SB:RF-P7Cav:Cylin3WT-Mon | [9 empty] | 0.5
8 | Disc 4 Water Temperature | SI | 02SB | RF | P7Cav | - | Disc4WT | Mon | SI-02SB:RF-P7Cav:Disc4WT-Mon | [9 empty] | 0.5
9 | Cell 4 Water Temperature | SI | 02SB | RF | P7Cav | - | Cylin4WT | Mon | SI-02SB:RF-P7Cav:Cylin4WT-Mon | [9 empty] | 0.5
10 | Coupler Water Temperature | SI | 02SB | RF | P7Cav | - | CoupWT | Mon | SI-02SB:RF-P7Cav:CoupWT-Mon | [9 empty] | 0.5
11 | Disc 5 Water Temperature | SI | 02SB | RF | P7Cav | - | Disc5WT | Mon | SI-02SB:RF-P7Cav:Disc5WT-Mon | [9 empty] | 0.5
12 | Cell 5 Water Temperature | SI | 02SB | RF | P7Cav | - | Cylin5WT | Mon | SI-02SB:RF-P7Cav:Cylin5WT-Mon | [9 empty] | 0.5
13 | Disc 6 Water Temperature | SI | 02SB | RF | P7Cav | - | Disc6WT | Mon | SI-02SB:RF-P7Cav:Disc6WT-Mon | [9 empty] | 0.5
14 | Cell 6 Water Temperature | SI | 02SB | RF | P7Cav | - | Cylin6WT | Mon | SI-02SB:RF-P7Cav:Cylin6WT-Mon | [9 empty] | 0.5
15 | Plunger 1 Water Temperature | SI | 02SB | RF | P7Cav | - | Pl1WT | Mon | SI-02SB:RF-P7Cav:Pl1WT-Mon | [9 empty] | 0.5
16 | Disc 7 Water Temperature | SI | 02SB | RF | P7Cav | - | Disc7WT | Mon | SI-02SB:RF-P7Cav:Disc7WT-Mon | [9 empty] | 0.5
17 | Cell 7 Water Temperature | SI | 02SB | RF | P7Cav | - | Cylin7WT | Mon | SI-02SB:RF-P7Cav:Cylin7WT-Mon | [9 empty] | 0.5
18 | Disc 8 Water Temperature | SI | 02SB | RF | P7Cav | - | Disc8WT | Mon | SI-02SB:RF-P7Cav:Disc8WT-Mon | [9 empty] | 0.5
19 | Water input Temperature | SI | 02SB | RF | P7Cav | - | WInT | Mon | SI-02SB:RF-P7Cav:WInT-Mon | [9 empty] | 0.5
20 | Disc 1 dTemperature | SI | 02SB | RF | P7Cav | - | Disc1WdT | Mon | SI-02SB:RF-P7Cav:Disc1WdT-Mon | [9 empty] | 0.5
21 | Disc 2 dTemperature | SI | 02SB | RF | P7Cav | - | Disc2WdT | Mon | SI-02SB:RF-P7Cav:Disc2WdT-Mon | [9 empty] | 0.5
22 | Disc 3 dTemperature | SI | 02SB | RF | P7Cav | - | Disc3WdT | Mon | SI-02SB:RF-P7Cav:Disc3WdT-Mon | [9 empty] | 0.5
23 | Disc 4 dTemperature | SI | 02SB | RF | P7Cav | - | Disc4WdT | Mon | SI-02SB:RF-P7Cav:Disc4WdT-Mon | [9 empty] | 0.5
24 | Disc 5 dTemperature | SI | 02SB | RF | P7Cav | - | Disc5WdT | Mon | SI-02SB:RF-P7Cav:Disc5WdT-Mon | [9 empty] | 0.5
25 | Disc 6 dTemperature | SI | 02SB | RF | P7Cav | - | DIsc6WdT | Mon | SI-02SB:RF-P7Cav:DIsc6WdT-Mon | [9 empty] | 0.5
26 | Disc 7 dTemperature | SI | 02SB | RF | P7Cav | - | DIsc7WdT | Mon | SI-02SB:RF-P7Cav:DIsc7WdT-Mon | [9 empty] | 0.5
27 | Disc 8 dTemperature | SI | 02SB | RF | P7Cav | - | Disc8WdT | Mon | SI-02SB:RF-P7Cav:Disc8WdT-Mon | [9 empty] | 0.5
28 | Cell 1 dTemperature | SI | 02SB | RF | P7Cav | - | Cell1WdT | Mon | SI-02SB:RF-P7Cav:Cell1WdT-Mon | [9 empty] | 0.5
29 | Cell 2 dTemperature | SI | 02SB | RF | P7Cav | - | Cell2WdT | Mon | SI-02SB:RF-P7Cav:Cell2WdT-Mon | [9 empty] | 0.5
30 | Cell 3 dTemperature | SI | 02SB | RF | P7Cav | - | Cell3WdT | Mon | SI-02SB:RF-P7Cav:Cell3WdT-Mon | [9 empty] | 0.5
31 | Cell 4 dTemperature | SI | 02SB | RF | P7Cav | - | Cell4WdT | Mon | SI-02SB:RF-P7Cav:Cell4WdT-Mon | [9 empty] | 0.5
32 | Cell 5 dTemperature | SI | 02SB | RF | P7Cav | - | Cell5WdT | Mon | SI-02SB:RF-P7Cav:Cell5WdT-Mon | [9 empty] | 0.5
33 | Cell 6 dTemperature | SI | 02SB | RF | P7Cav | - | Cell6WdT | Mon | SI-02SB:RF-P7Cav:Cell6WdT-Mon | [9 empty] | 0.5
34 | Cell 7 dTemperature | SI | 02SB | RF | P7Cav | - | Cell7WdT | Mon | SI-02SB:RF-P7Cav:Cell7WdT-Mon | [9 empty] | 0.5
35 | Disc 1 Flow Rate | SI | 02SB | RF | P7Cav | - | Disc1FlwRt | Mon | SI-02SB:RF-P7Cav:Disc1FlwRt-Mon | [9 empty] | 0.5
36 | Disc 2 Flow Rate | SI | 02SB | RF | P7Cav | - | Disc2FlwRt | Mon | SI-02SB:RF-P7Cav:Disc2FlwRt-Mon | [9 empty] | 0.5
37 | Disc 3 Flow Rate | SI | 02SB | RF | P7Cav | - | Disc3FlwRt | Mon | SI-02SB:RF-P7Cav:Disc3FlwRt-Mon | [9 empty] | 0.5
38 | Disc 4 Flow Rate | SI | 02SB | RF | P7Cav | - | Disc4FlwRt | Mon | SI-02SB:RF-P7Cav:Disc4FlwRt-Mon | [9 empty] | 0.5
39 | Disc 5 Flow Rate | SI | 02SB | RF | P7Cav | - | Disc5FlwRt | Mon | SI-02SB:RF-P7Cav:Disc5FlwRt-Mon | [9 empty] | 0.5
40 | Disc 6 Flow Rate | SI | 02SB | RF | P7Cav | - | DIsc6FlwRt | Mon | SI-02SB:RF-P7Cav:DIsc6FlwRt-Mon | [9 empty] | 0.5
41 | Disc 7 Flow Rate | SI | 02SB | RF | P7Cav | - | DIsc7FlwRt | Mon | SI-02SB:RF-P7Cav:DIsc7FlwRt-Mon | [9 empty] | 0.5
42 | Disc 8 Flow Rate | SI | 02SB | RF | P7Cav | - | Disc8FlwRt | Mon | SI-02SB:RF-P7Cav:Disc8FlwRt-Mon | [9 empty] | 0.5
43 | Cell 1 Flow Rate | SI | 02SB | RF | P7Cav | - | Cell1FlwRt | Mon | SI-02SB:RF-P7Cav:Cell1FlwRt-Mon | [9 empty] | 0.5
44 | Cell 2 Flow Rate | SI | 02SB | RF | P7Cav | - | Cell2FlwRt | Mon | SI-02SB:RF-P7Cav:Cell2FlwRt-Mon | [9 empty] | 0.5
45 | Cell 3 Flow Rate | SI | 02SB | RF | P7Cav | - | Cell3FlwRt | Mon | SI-02SB:RF-P7Cav:Cell3FlwRt-Mon | [9 empty] | 0.5
46 | Cell 4 Flow Rate | SI | 02SB | RF | P7Cav | - | Cell4FlwRt | Mon | SI-02SB:RF-P7Cav:Cell4FlwRt-Mon | [9 empty] | 0.5
47 | Cell 5 Flow Rate | SI | 02SB | RF | P7Cav | - | Cell5FlwRt | Mon | SI-02SB:RF-P7Cav:Cell5FlwRt-Mon | [9 empty] | 0.5
48 | Cell 6 Flow Rate | SI | 02SB | RF | P7Cav | - | Cell6FlwRt | Mon | SI-02SB:RF-P7Cav:Cell6FlwRt-Mon | [9 empty] | 0.5
49 | Cell 7 Flow Rate | SI | 02SB | RF | P7Cav | - | Cell7FlwRt | Mon | SI-02SB:RF-P7Cav:Cell7FlwRt-Mon | [9 empty] | 0.5
50 | Disc 1 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissDisc1 | Mon | SI-02SB:RF-P7Cav:PwrDissDisc1-Mon | [9 empty] | 0.5
51 | Disc 2 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissDisc2 | Mon | SI-02SB:RF-P7Cav:PwrDissDisc2-Mon | [9 empty] | 0.5
52 | Disc 3 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissDisc3 | Mon | SI-02SB:RF-P7Cav:PwrDissDisc3-Mon | [9 empty] | 0.5
53 | Disc 4 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissDisc4 | Mon | SI-02SB:RF-P7Cav:PwrDissDisc4-Mon | [9 empty] | 0.5
54 | Disc 5 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissDisc5 | Mon | SI-02SB:RF-P7Cav:PwrDissDisc5-Mon | [9 empty] | 0.5
55 | Disc 6 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissDIsc6 | Mon | SI-02SB:RF-P7Cav:PwrDissDIsc6-Mon | [9 empty] | 0.5
56 | Disc 7 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissDIsc7 | Mon | SI-02SB:RF-P7Cav:PwrDissDIsc7-Mon | [9 empty] | 0.5
57 | Disc 8 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissDisc8 | Mon | SI-02SB:RF-P7Cav:PwrDissDisc8-Mon | [9 empty] | 0.5
58 | Cell 1 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissCell1 | Mon | SI-02SB:RF-P7Cav:PwrDissCell1-Mon | [9 empty] | 0.5
59 | Cell 2 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissCell2 | Mon | SI-02SB:RF-P7Cav:PwrDissCell2-Mon | [9 empty] | 0.5
60 | Cell 3 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissCell3 | Mon | SI-02SB:RF-P7Cav:PwrDissCell3-Mon | [9 empty] | 0.5
61 | Cell 4 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissCell4 | Mon | SI-02SB:RF-P7Cav:PwrDissCell4-Mon | [9 empty] | 0.5
62 | Cell 5 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissCell5 | Mon | SI-02SB:RF-P7Cav:PwrDissCell5-Mon | [9 empty] | 0.5
63 | Cell 6 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissCell6 | Mon | SI-02SB:RF-P7Cav:PwrDissCell6-Mon | [9 empty] | 0.5
64 | Cell 7 Power Dissipated | SI | 02SB | RF | P7Cav | - | PwrDissCell7 | Mon | SI-02SB:RF-P7Cav:PwrDissCell7-Mon | [9 empty] | 0.5
65 | Cell 1 Water Power | SI | 02SB | RF | P7Cav | - | PwrWtCell1 | Mon | SI-02SB:RF-P7Cav:PwrWtCell1-Mon | [9 empty] | 0.5
66 | Cell 2 Water Power | SI | 02SB | RF | P7Cav | - | PwrWtCell2 | Mon | SI-02SB:RF-P7Cav:PwrWtCell2-Mon | [9 empty] | 0.5
67 | Cell 3 Water Power | SI | 02SB | RF | P7Cav | - | PwrWtCell3 | Mon | SI-02SB:RF-P7Cav:PwrWtCell3-Mon | [9 empty] | 0.5
68 | Cell 4 Water Power | SI | 02SB | RF | P7Cav | - | PwrWtCell4 | Mon | SI-02SB:RF-P7Cav:PwrWtCell4-Mon | [9 empty] | 0.5
69 | Cell 5 Water Power | SI | 02SB | RF | P7Cav | - | PwrWtCell5 | Mon | SI-02SB:RF-P7Cav:PwrWtCell5-Mon | [9 empty] | 0.5
70 | Cell 6 Water Power | SI | 02SB | RF | P7Cav | - | PwrWtCell6 | Mon | SI-02SB:RF-P7Cav:PwrWtCell6-Mon | [9 empty] | 0.5
71 | Cell 7 Water Power | SI | 02SB | RF | P7Cav | - | PwrWtCell7 | Mon | SI-02SB:RF-P7Cav:PwrWtCell7-Mon | [9 empty] | 0.5
72 | Total Water Power | SI | 02SB | RF | P7Cav | - | PwrWtTotal | Mon | SI-02SB:RF-P7Cav:PwrWtTotal-Mon | [9 empty] | 0.5
73 | Total Water Power dBm | SI | 02SB | RF | P7Cav | - | PwrWtTotaldBm | Mon | SI-02SB:RF-P7Cav:PwrWtTotaldBm-Mon | [9 empty] | 0.5
74 | Cell 1 Voltage Relation | SI | 02SB | RF | P7Cav | - | VrCell1 | Mon | SI-02SB:RF-P7Cav:VrCell1-Mon | [9 empty] | 0.5
75 | Cell 2 Voltage Relation | SI | 02SB | RF | P7Cav | - | VrCell2 | Mon | SI-02SB:RF-P7Cav:VrCell2-Mon | [9 empty] | 0.5
76 | Cell 3 Voltage Relation | SI | 02SB | RF | P7Cav | - | VrCell3 | Mon | SI-02SB:RF-P7Cav:VrCell3-Mon | [9 empty] | 0.5
77 | Cell 4 Voltage Relation | SI | 02SB | RF | P7Cav | - | VrCell4 | Mon | SI-02SB:RF-P7Cav:VrCell4-Mon | [9 empty] | 0.5
78 | Cell 5 Voltage Relation | SI | 02SB | RF | P7Cav | - | VrCell5 | Mon | SI-02SB:RF-P7Cav:VrCell5-Mon | [9 empty] | 0.5
79 | Cell 6 Voltage Relation | SI | 02SB | RF | P7Cav | - | VrCell6 | Mon | SI-02SB:RF-P7Cav:VrCell6-Mon | [9 empty] | 0.5
80 | Cell 7 Voltage Relation | SI | 02SB | RF | P7Cav | - | VrCell7 | Mon | SI-02SB:RF-P7Cav:VrCell7-Mon | [9 empty] | 0.5

## LLRF
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Interlock LLRF | RA | RaSIA01 | RF | LLRF | - | Intlk | Mon | RA-RaSIA01:RF-LLRF:Intlk-Mon | N/A | N/A | RA_RaSIA01_RF_LLRF_IntlkMon | Digital | Input |  |  |  | RA_RaSIA01_RF_LLRF_IntlkMon | .1
2 | PT- 100 01 Pré-Amplificador | RA | RaSIA01 | RF | LLRFPreAmp | 1 | T1 | Mon | RA-RaSIA01:RF-LLRFPreAmp-1:T1-Mon | RA-RaSIA01:RF-LLRFPreAmp-1:T1UpperLimit-Cte | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_T1Mon | Analog | Input | Set_Temp[4] | N/A | C | RA_RaSIA01_RF_LLRFPreAmp_1_T1Mon | .5 | 2
3 | PT- 100 02 Pré-Amplificador | RA | RaSIA01 | RF | LLRFPreAmp | 1 | T2 | Mon | RA-RaSIA01:RF-LLRFPreAmp-1:T2-Mon | RA-RaSIA01:RF-LLRFPreAmp-1:T2UpperLimit-Cte | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_T2Mon | Analog | Input | Set_Temp[4] | N/A | C | RA_RaSIA01_RF_LLRFPreAmp_1_T2Mon | .5 | 2
4 | Chave Pin Lenta Torre 01 | RA | RaSIA01 | RF | LLRFPreAmp | 1 | PINSw1 | Mon | RA-RaSIA01:RF-LLRFPreAmp-1:PINSw1-Mon | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw1Mon | Digital | Output |  |  |  | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw1Mon | .1
5 | Chave Pin Lenta Torre 02 | RA | RaSIA01 | RF | LLRFPreAmp | 1 | PINSw2 | Mon | RA-RaSIA01:RF-LLRFPreAmp-1:PINSw2-Mon | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw2Mon | Digital | Output |  |  |  | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw2Mon | .1
6 | Habilita Chave Pin 01 | RA | RaSIA01 | RF | LLRFPreAmp | 1 | PINSw1Enbl | Cmd | RA-RaSIA01:RF-LLRFPreAmp-1:PINSw1Enbl-Cmd | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw1EnblCmd | Digital | Control |  |  |  | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw1EnblCmd | .1
7 | Habilita Chave Pin 02 | RA | RaSIA01 | RF | LLRFPreAmp | 1 | PINSw2Enbl | Cmd | RA-RaSIA01:RF-LLRFPreAmp-1:PINSw2Enbl-Cmd | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw2EnblCmd | Digital | Control |  |  |  | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw2EnblCmd | .1
8 | Desabilita Chave Pin 01 | RA | RaSIA01 | RF | LLRFPreAmp | 1 | PINSw1Dsbl | Cmd | RA-RaSIA01:RF-LLRFPreAmp-1:PINSw1Dsbl-Cmd | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw1DsblCmd | Digital | Control |  |  |  | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw1DsblCmd | .1
9 | Desabilita Chave Pin 02 | RA | RaSIA01 | RF | LLRFPreAmp | 1 | PINSw2Dsbl | Cmd | RA-RaSIA01:RF-LLRFPreAmp-1:PINSw2Dsbl-Cmd | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw2DsblCmd | Digital | Control |  |  |  | RA_RaSIA01_RF_LLRFPreAmp_1_PINSw2DsblCmd | .1
10 | PT- 100 01 Pré-Amplificador Temperatura acima do Set | RA | RaSIA01 | RF | LLRFPreAmp | 1 | T1Up | Mon | RA-RaSIA01:RF-LLRFPreAmp-1:T1Up-Mon | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_T1UpMon | Digital | Input |  |  |  | RA_RaSIA01_RF_LLRFPreAmp_1_T1UpMon | .1
11 | PT- 100 02 Pré-Amplificador Temperatura acima do Set | RA | RaSIA01 | RF | LLRFPreAmp | 1 | T2Up | Mon | RA-RaSIA01:RF-LLRFPreAmp-1:T2Up-Mon | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_1_T2UpMon | Digital | Input |  |  |  | RA_RaSIA01_RF_LLRFPreAmp_1_T2UpMon | .1
12 | LLRF AES Ligado | RA | ToSIA | RF | SSAmpTower | - | RFOn | Mon | RA-ToSIA:RF-SSAmpTower:RFOn-Mon | N/A | N/A | RA_ToSIA_RF_SSAmpTower_RFOnMon | Digital | Output |  |  |  | RA_ToSIA_RF_SSAmpTower_RFOnMon | .1
13 | PT- 100 01 Pré-Amplificador 02 | RA | RaSIA01 | RF | LLRFPreAmp | 2 | T1 | Mon | RA-RaSIA01:RF-LLRFPreAmp-2:T1-Mon | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_T1Mon | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_T1Mon
14 | PT- 100 02 Pré-Amplificador 02 | RA | RaSIA01 | RF | LLRFPreAmp | 2 | T2 | Mon | RA-RaSIA01:RF-LLRFPreAmp-2:T2-Mon | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_T2Mon | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_T2Mon
15 | Chave Pin Lenta Torre 03 | RA | RaSIA01 | RF | LLRFPreAmp | 2 | PINSw1 | Mon | RA-RaSIA01:RF-LLRFPreAmp-2:PINSw1-Mon | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_PINSw1Mon | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_PINSw1Mon
16 | Chave Pin Lenta Torre 04 | RA | RaSIA01 | RF | LLRFPreAmp | 2 | PINSw2 | Mon | RA-RaSIA01:RF-LLRFPreAmp-2:PINSw2-Mon | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_PINSw2Mon | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_PINSw2Mon
17 | Habilita Chave Pin 03 | RA | RaSIA01 | RF | LLRFPreAmp | 2 |  |  | RA-RaSIA01:RF-LLRFPreAmp-2:- | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_ | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_
18 | Habilita Chave Pin 04 | RA | RaSIA01 | RF | LLRFPreAmp | 2 |  |  | RA-RaSIA01:RF-LLRFPreAmp-2:- | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_ | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_
19 | Desabilita Chave Pin 03 | RA | RaSIA01 | RF | LLRFPreAmp | 2 |  |  | RA-RaSIA01:RF-LLRFPreAmp-2:- | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_ | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_
20 | Desabilita Chave Pin 04 | RA | RaSIA01 | RF | LLRFPreAmp | 2 |  |  | RA-RaSIA01:RF-LLRFPreAmp-2:- | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_ | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_
21 | PT- 100 01 Pré-Amplificador 02 Temperatura acima do Set | RA | RaSIA01 | RF | LLRFPreAmp | 2 |  |  | RA-RaSIA01:RF-LLRFPreAmp-2:- | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_ | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_
22 | PT- 100 02 Pré-Amplificador 02 Temperatura acima do Set | RA | RaSIA01 | RF | LLRFPreAmp | 2 |  |  | RA-RaSIA01:RF-LLRFPreAmp-2:- | N/A | N/A | RA_RaSIA01_RF_LLRFPreAmp_2_ | [5 empty] | RA_RaSIA01_RF_LLRFPreAmp_2_

## Legenda
Variável que tenho dúvida
Variável foi alterada e alteração não foi adicionada no CLP
Variável foi alterada e alteração não foi adicionada no IOC
Variável não existe
Variavel no controlador porém não foi adicionada no CLP