## Interlock
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Interlock Sirius | RA | RaBO02 | RF | IntlkCtrl | - | IntlkSirius | Mon | RA-RaBO02:RF-IntlkCtrl:IntlkSirius-Mon |  |  | RA_RaBO02_RF_IntlkCtrl_IntlkSiriusMon | Digital | Input |  |  |  | RA_RaBO02_RF_IntlkCtrl_IntlkSiriusMon | .1
2 | Sinal de erro do CLP para o LLRF | RA | RaBO02 | RF | IntlkCtrl | - | IntlkLLRF | Mon | RA-RaBO02:RF-IntlkCtrl:IntlkLLRF-Mon |  |  | RA_RaBO02_RF_IntlkCtrl_IntlkLLRFMon | Digital | Output |  |  |  | RA_RaBO02_RF_IntlkCtrl_IntlkLLRFMon | .1
3 | Sinal SSA Ligado para LLRF | BO | 05D | RF | Intlk | - | SSAOn | Mon | BO-05D:RF-Intlk:SSAOn-Mon |  |  | BO_05D_RF_Intlk_SSAOnMon | Digital | Output |  |  |  | BO_05D_RF_Intlk_SSAOnMon | .1
4 | Emergencia sistema de interlock | BO | 05D | RF | Intlk | - | EStop | Mon | BO-05D:RF-Intlk:EStop-Mon |  |  | BO_05D_RF_Intlk_EStopMon | Digital | Input |  |  |  | BO_05D_RF_Intlk_EStopMon | .1
5 | Reset de Falhas | RA | RaBO02 | RF | Intlk | - | Reset | Cmd | RA-RaBO02:RF-Intlk:Reset-Cmd |  |  | RA_RaBO02_RF_Intlk_ResetCmd | Digital | Control |  |  |  | RA_RaBO02_RF_Intlk_ResetCmd | .1

## Transmission Line
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Detector de Arco | RA | TLBO | RF | Circulator | - | Arc | Mon | RA-TLBO:RF-Circulator:Arc-Mon |  |  | RA_TLBO_RF_Circulator_ArcMon | Digital | Input |  |  |  | RA_TLBO_RF_Circulator_ArcMon | .1
2 | Detector de Arco Sistema A Analogico | RA | RaBO02 | RF | ArcDetec | Circ | Analog | Mon | N/A |  |  | N/A | N/A | N/A |  |  |  | N/A | .1
3 | Teste detector de Arco | RA | RaBO02 | RF | ArcDetec | Circ | Test | Sel | RA-RaBO02:RF-ArcDetec-Circ:Test-Sel |  |  | RA_RaBO02_RF_ArcDetec_Circ_TestSel | Digital | Control |  |  |  | RA_RaBO02_RF_ArcDetec_Circ_TestSel | .1
4 | Leitura Teste Detector de Arco | RA | RaBO02 | RF | ArcDetec | Circ | Test | Sts | RA-RaBO02:RF-ArcDetec-Circ:Test-Sts |  |  | RA_RaBO02_RF_ArcDetec_Circ_TestSts | Digital | Input |  |  |  | RA_RaBO02_RF_ArcDetec_Circ_TestSts | .1
5 | Sistema de Interlock circulador operacional | RA | TLBO | RF | Circulator | - | IntlkOp | Mon | RA-TLBO:RF-Circulator:IntlkOp-Mon |  |  | RA_TLBO_RF_Circulator_IntlkOpMon | Digital | Input |  |  |  | RA_TLBO_RF_Circulator_IntlkOpMon | .1
6 | Vazão Circulador - Via Skid | RA | TLBO | RF | Circulator | - | FlwRt | Mon | RA-TLBO:RF-Circulator:FlwRt-Mon |  |  | RA_TLBO_RF_Circulator_FlwRtMon | Digital | Input |  |  |  | RA_TLBO_RF_Circulator_FlwRtMon | .1
7 | Bobinas do circulador | RA | TLBO | RF | Circulator | - | Sts | Mon | RA-TLBO:RF-Circulator:Sts-Mon |  |  | RA_TLBO_RF_Circulator_StsMon | Digital | Input |  |  |  | RA_TLBO_RF_Circulator_StsMon | .1
8 | Temp. do Circulador Abaixo do Set | RA | TLBO | RF | Circulator | - | TinDown | Mon | RA-TLBO:RF-Circulator:TinDown-Mon |  |  | RA_TLBO_RF_Circulator_TinDownMon | Digital | Input |  |  |  | RA_TLBO_RF_Circulator_TinDownMon | .1
9 | Temp. do Circulador Acima do Set | RA | TLBO | RF | Circulator | - | TinUp | Mon | RA-TLBO:RF-Circulator:TinUp-Mon |  |  | RA_TLBO_RF_Circulator_TinUpMon | Digital | Input |  |  |  | RA_TLBO_RF_Circulator_TinUpMon | .1
10 | Drift de Temp muito Alto | RA | TLBO | RF | Circulator | - | TDrift | Mon | RA-TLBO:RF-Circulator:TDrift-Mon |  |  | RA_TLBO_RF_Circulator_TDriftMon | Digital | Input |  |  |  | RA_TLBO_RF_Circulator_TDriftMon | .1
11 | Temp. Ambiente Abaixo do Set | RA | TLBO | RF | Circulator | - | TEnv | Mon | RA-TLBO:RF-Circulator:TEnv-Mon |  |  | RA_TLBO_RF_Circulator_TEnvMon | Digital | Input |  |  |  | RA_TLBO_RF_Circulator_TEnvMon | .1
12 | Vazão Carga 70kW | RA | TLBO | RF | Load | - | FlwRt | Mon | RA-TLBO:RF-Load:FlwRt-Mon |  |  | RA_TLBO_RF_Load_FlwRtMon | Digital | Input |  |  |  | RA_TLBO_RF_Load_FlwRtMon | .1
13 | Interlock geral Circulador | RA | TLBO | RF | Circulator | - | Sts | Mon | N/A |  |  | N/A | N/A | N/A |  |  |  | N/A | .1
14 | Interlock geral Linha de Transmissao | RA | TLBO | RF | TrLine | - | Sts | Mon | RA-TLBO:RF-TrLine:Sts-Mon |  |  | RA_TLBO_RF_TrLine_StsMon | Digital | Control |  |  |  | RA_TLBO_RF_TrLine_StsMon | .1
15 | Reset Detector de Arco | RA | RaBO02 | RF | ArcDetec | Circ | Reset | Mon | RA-RaBO02:RF-ArcDetec-Circ:Reset-Mon |  |  | RA_RaBO02_RF_ArcDetec_Circ_ResetMon | Digital | Output |  |  |  | RA_RaBO02_RF_ArcDetec_Circ_ResetMon | .1
16 | Detector de Arco Power Fail Out | RA | RaBO02 | RF | ArcDetec | Circ | PwrFail | Mon | RA-RaBO02:RF-ArcDetec-Circ:PwrFail-Mon |  |  | RA_RaBO02_RF_ArcDetec_Circ_PwrFailMon | Digital | Input |  |  |  | RA_RaBO02_RF_ArcDetec_Circ_PwrFailMon | .1

## SSAmp Tower
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Monitoramento 300Vdc habilitado | RA | ToBO | RF | ACDCPanel | - | 300VdcEnbl | Mon | RA-ToBO:RF-ACDCPanel:300VdcEnbl-Mon | N/A | N/A | RA_ToBO_RF_ACDCPanel_300VdcEnblMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_ACDCPanel_300VdcEnblMon | .1 | 2
2 | Desliga 300VDC | RA | ToBO | RF | ACDCPanel | - | 300VdcDsbl | Sel | RA-ToBO:RF-ACDCPanel:300VdcDsbl-Sel | N/A | N/A | RA_ToBO_RF_ACDCPanel_300VdcDsblSel | Digital | Control | N/A | N/A |  | RA_ToBO_RF_ACDCPanel_300VdcDsblSel | .1 | 2
3 | Liga 300 VDC | RA | ToBO | RF | ACDCPanel | - | 300VdcEnbl | Sel | RA-ToBO:RF-ACDCPanel:300VdcEnbl-Sel | N/A | N/A | RA_ToBO_RF_ACDCPanel_300VdcEnblSel | Digital | Control | N/A | N/A |  | RA_ToBO_RF_ACDCPanel_300VdcEnblSel | .1 | 2
4 | Leitura Liga 300 VDC | RA | ToBO | RF | ACDCPanel | - | 300Vdc | Sts | RA-ToBO:RF-ACDCPanel:300Vdc-Sts | N/A | N/A | RA_ToBO_RF_ACDCPanel_300VdcSts | Digital | Output | N/A | N/A |  | RA_ToBO_RF_ACDCPanel_300VdcSts | .1 | 2
5 | Termostato Barra Dissipadora 01 | RA | ToBO | RF | HeatSink | H01 | Tms | Mon | RA-ToBO:RF-HeatSink-H01:Tms-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H01_TmsMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H01_TmsMon | .1 | 2
6 | Termostato Barra Dissipadora 02 | RA | ToBO | RF | HeatSink | H02 | Tms | Mon | RA-ToBO:RF-HeatSink-H02:Tms-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H02_TmsMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H02_TmsMon | .1 | 2
7 | Termostato Barra Dissipadora 03 | RA | ToBO | RF | HeatSink | H03 | Tms | Mon | RA-ToBO:RF-HeatSink-H03:Tms-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H03_TmsMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H03_TmsMon | .1 | 2
8 | Termostato Barra Dissipadora 04 | RA | ToBO | RF | HeatSink | H04 | Tms | Mon | RA-ToBO:RF-HeatSink-H04:Tms-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H04_TmsMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H04_TmsMon | .1 | 2
9 | Termostato Barra Dissipadora 05 | RA | ToBO | RF | HeatSink | H05 | Tms | Mon | RA-ToBO:RF-HeatSink-H05:Tms-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H05_TmsMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H05_TmsMon | .1 | 2
10 | Termostato Barra Dissipadora 06 | RA | ToBO | RF | HeatSink | H06 | Tms | Mon | RA-ToBO:RF-HeatSink-H06:Tms-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H06_TmsMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H06_TmsMon | .1 | 2
11 | PT - 100 Barra Dissipadora 01 | RA | ToBO | RF | HeatSink | H01 | T | Mon | RA-ToBO:RF-HeatSink-H01:T-Mon | RA-ToBO:RF-HeatSink-H01:TUpperLimit-Cte | RA-ToBO:RF-HeatSink-H01:TLowerLimit-Cte | RA_ToBO_RF_HeatSink_H01_TMon | Analog | Input | Set_Temp[3] | Set_Temp[2] | C | RA_ToBO_RF_HeatSink_H01_TMon | .5 | 2
12 | PT - 100 Barra Dissipadora 02 | RA | ToBO | RF | HeatSink | H02 | T | Mon | RA-ToBO:RF-HeatSink-H02:T-Mon | RA-ToBO:RF-HeatSink-H02:TUpperLimit-Cte | RA-ToBO:RF-HeatSink-H02:TLowerLimit-Cte | RA_ToBO_RF_HeatSink_H02_TMon | Analog | Input | Set_Temp[3] | Set_Temp[2] | C | RA_ToBO_RF_HeatSink_H02_TMon | .5 | 2
13 | PT - 100 Barra Dissipadora 03 | RA | ToBO | RF | HeatSink | H03 | T | Mon | RA-ToBO:RF-HeatSink-H03:T-Mon | RA-ToBO:RF-HeatSink-H03:TUpperLimit-Cte | RA-ToBO:RF-HeatSink-H03:TLowerLimit-Cte | RA_ToBO_RF_HeatSink_H03_TMon | Analog | Input | Set_Temp[3] | Set_Temp[2] | C | RA_ToBO_RF_HeatSink_H03_TMon | .5 | 2
14 | PT - 100 Barra Dissipadora 04 | RA | ToBO | RF | HeatSink | H04 | T | Mon | RA-ToBO:RF-HeatSink-H04:T-Mon | RA-ToBO:RF-HeatSink-H04:TUpperLimit-Cte | RA-ToBO:RF-HeatSink-H04:TLowerLimit-Cte | RA_ToBO_RF_HeatSink_H04_TMon | Analog | Input | Set_Temp[3] | Set_Temp[2] | C | RA_ToBO_RF_HeatSink_H04_TMon | .5 | 2
15 | PT - 100 Barra Dissipadora 05 | RA | ToBO | RF | HeatSink | H05 | T | Mon | RA-ToBO:RF-HeatSink-H05:T-Mon | RA-ToBO:RF-HeatSink-H05:TUpperLimit-Cte | RA-ToBO:RF-HeatSink-H05:TLowerLimit-Cte | RA_ToBO_RF_HeatSink_H05_TMon | Analog | Input | Set_Temp[3] | Set_Temp[2] | C | RA_ToBO_RF_HeatSink_H05_TMon | .5 | 2
16 | PT - 100 Barra Dissipadora 06 | RA | ToBO | RF | HeatSink | H06 | T | Mon | RA-ToBO:RF-HeatSink-H06:T-Mon | RA-ToBO:RF-HeatSink-H06:TUpperLimit-Cte | RA-ToBO:RF-HeatSink-H06:TLowerLimit-Cte | RA_ToBO_RF_HeatSink_H06_TMon | Analog | Input | Set_Temp[3] | Set_Temp[2] | C | RA_ToBO_RF_HeatSink_H06_TMon | .5 | 2
17 | Interlock temperatura acima do set Barra Dissipadora 01 | RA | ToBO | RF | HeatSink | H01 | TUp | Mon | RA-ToBO:RF-HeatSink-H01:TUp-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H01_TUpMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H01_TUpMon | .1 | 2
18 | Interlock temperatura acima do set Barra Dissipadora 02 | RA | ToBO | RF | HeatSink | H02 | TUp | Mon | RA-ToBO:RF-HeatSink-H02:TUp-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H02_TUpMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H02_TUpMon | .1 | 2
19 | Interlock temperatura acima do set Barra Dissipadora 03 | RA | ToBO | RF | HeatSink | H03 | TUp | Mon | RA-ToBO:RF-HeatSink-H03:TUp-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H03_TUpMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H03_TUpMon | .1 | 2
20 | Interlock temperatura acima do set Barra Dissipadora 04 | RA | ToBO | RF | HeatSink | H04 | TUp | Mon | RA-ToBO:RF-HeatSink-H04:TUp-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H04_TUpMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H04_TUpMon | .1 | 2
21 | Interlock temperatura acima do set Barra Dissipadora 05 | RA | ToBO | RF | HeatSink | H05 | TUp | Mon | RA-ToBO:RF-HeatSink-H05:TUp-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H05_TUpMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H05_TUpMon | .1 | 2
22 | Interlock temperatura acima do set Barra Dissipadora 06 | RA | ToBO | RF | HeatSink | H06 | TUp | Mon | RA-ToBO:RF-HeatSink-H06:TUp-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H06_TUpMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H06_TUpMon | .1 | 2
23 | Interlock temperatura abaixo do set Barra Dissipadora 01 | RA | ToBO | RF | HeatSink | H01 | TDown | Mon | RA-ToBO:RF-HeatSink-H01:TDown-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H01_TDownMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H01_TDownMon | .1 | 2
24 | Interlock temperatura abaixo do set Barra Dissipadora 02 | RA | ToBO | RF | HeatSink | H02 | TDown | Mon | RA-ToBO:RF-HeatSink-H02:TDown-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H02_TDownMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H02_TDownMon | .1 | 2
25 | Interlock temperatura abaixo do set Barra Dissipadora 03 | RA | ToBO | RF | HeatSink | H03 | TDown | Mon | RA-ToBO:RF-HeatSink-H03:TDown-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H03_TDownMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H03_TDownMon | .1 | 2
26 | Interlock temperatura abaixo do set Barra Dissipadora 04 | RA | ToBO | RF | HeatSink | H04 | TDown | Mon | RA-ToBO:RF-HeatSink-H04:TDown-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H04_TDownMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H04_TDownMon | .1 | 2
27 | Interlock temperatura abaixo do set Barra Dissipadora 05 | RA | ToBO | RF | HeatSink | H05 | TDown | Mon | RA-ToBO:RF-HeatSink-H05:TDown-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H05_TDownMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H05_TDownMon | .1 | 2
28 | Interlock temperatura abaixo do set Barra Dissipadora 06 | RA | ToBO | RF | HeatSink | H06 | TDown | Mon | RA-ToBO:RF-HeatSink-H06:TDown-Mon | N/A | N/A | RA_ToBO_RF_HeatSink_H06_TDownMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_HeatSink_H06_TDownMon | .1 | 2
30 | Vazão Rotâmetro - via Skid | RA | ToBO | RF | SSAmpTower | - | HdFlwRt | Mon | RA-ToBO:RF-SSAmpTower:HdFlwRt-Mon | N/A | N/A | RA_ToBO_RF_SSAmpTower_HdFlwRtMon | Digital | Input | N/A | N/A |  | RA_ToBO_RF_SSAmpTower_HdFlwRtMon | .1 | 2
31 | Desliga Conversores DC/DC | RA | ToBO | RF | SSAmpTower | - | PwrCnvDsbl | Sel | RA-ToBO:RF-SSAmpTower:PwrCnvDsbl-Sel | N/A | N/A | RA_ToBO_RF_SSAmpTower_PwrCnvDsblSel | Digital | Control | N/A | N/A |  | RA_ToBO_RF_SSAmpTower_PwrCnvDsblSel | .1 | 2
29 | Liga Conversores DC/DC | RA | ToBO | RF | SSAmpTower | - | PwrCnvEnbl | Sel | RA-ToBO:RF-SSAmpTower:PwrCnvEnbl-Sel | N/A | N/A | RA_ToBO_RF_SSAmpTower_PwrCnvEnblSel | Digital | Control | N/A | N/A |  | RA_ToBO_RF_SSAmpTower_PwrCnvEnblSel | .1 | 2
30 | Leitura Conversores DC/DC | RA | ToBO | RF | SSAmpTower | - | PwrCnv | Sts | RA-ToBO:RF-SSAmpTower:PwrCnv-Sts | N/A | N/A | RA_ToBO_RF_SSAmpTower_PwrCnvSts | Digital | Output | N/A | N/A |  | RA_ToBO_RF_SSAmpTower_PwrCnvSts | .1 | 2
34 | Interlock Geral SSA | RA | ToBO | RF | SSAmpTower | - | Sts | Mon | RA-ToBO:RF-SSAmpTower:Sts-Mon | N/A | N/A | RA_ToBO_RF_SSAmpTower_StsMon | Digital | Control | N/A | N/A |  | RA_ToBO_RF_SSAmpTower_StsMon | .1 | 2
35 | Corrente AC/DC | BO | ToBO | RF | ACDCPanel | - | CurrentVdc | Mon_RAW | BO-ToBO:RF-ACDCPanel:CurrentVdc-Mon_RAW | N/A | N/A | BO_ToBO_RF_ACDCPanel_CurrentVdcMon_RAW | Analog | Input | N/A | N/A | A | BO_ToBO_RF_ACDCPanel_CurrentVdcMon_RAW | .1 | 2
36 | Tensão AC/DC | BO | ToBO | RF | ACDCPanel | - | 300Vdc | Mon_RAW | BO-ToBO:RF-ACDCPanel:300Vdc-Mon_RAW | N/A | N/A | BO_ToBO_RF_ACDCPanel_300VdcMon_RAW | Analog | Input | N/A | N/A | V | BO_ToBO_RF_ACDCPanel_300VdcMon_RAW | .1 | 2
37 | Local Remoto Painel AC DC | BO | ToBO | RF | ACDCPanel | - | CtrlMode | Mon | BO-ToBO:RF-ACDCPanel:CtrlMode-Mon | N/A | N/A | BO_ToBO_RF_ACDCPanel_CtrlModeMon | Digital | Input | N/A | N/A |  | BO_ToBO_RF_ACDCPanel_CtrlModeMon | .1 | 2
38 | Falha Painel AC DC | BO | ToBO | RF | ACDCPanel | - | Intlk | Mon | BO-ToBO:RF-ACDCPanel:Intlk-Mon | N/A | N/A | BO_ToBO_RF_ACDCPanel_IntlkMon | Digital | Input | N/A | N/A |  | BO_ToBO_RF_ACDCPanel_IntlkMon | .1 | 2

## LLRF
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Habilita Chave Pin Lenta | RA | RaBO01 | RF | LLRFPreAmp | - | PinSwEnbl | Cmd | RA-RaBO01:RF-LLRFPreAmp:PinSwEnbl-Cmd | N/A | N/A | RA_RaBO01_RF_LLRFPreAmp_PinSwEnblCmd | Digital | Control |  |  |  | RA_RaBO01_RF_LLRFPreAmp_PinSwEnblCmd | .1
2 | Desabilita Chave Pin Lenta | RA | RaBO01 | RF | LLRFPreAmp | - | PinSwDsbl | Cmd | RA-RaBO01:RF-LLRFPreAmp:PinSwDsbl-Cmd | N/A | N/A | RA_RaBO01_RF_LLRFPreAmp_PinSwDsblCmd | Digital | Control |  |  |  | RA_RaBO01_RF_LLRFPreAmp_PinSwDsblCmd | .1
3 | Chave Pin Lenta readback | RA | RaBO01 | RF | LLRFPreAmp | - | PinSw | Sts | RA-RaBO01:RF-LLRFPreAmp:PinSw-Sts | N/A | N/A | RA_RaBO01_RF_LLRFPreAmp_PinSwSts | [5 empty] | N/A | .1
4 | Chave Pin Lenta | RA | RaBO01 | RF | LLRFPreAmp | - | PinSw | Mon | RA-RaBO01:RF-LLRFPreAmp:PinSw-Mon | N/A | N/A | RA_RaBO01_RF_LLRFPreAmp_PinSwMon | Digital | Output |  |  |  | RA_RaBO01_RF_LLRFPreAmp_PinSwMon | .1
5 | LLRF Operacional | RA | RaBO01 | RF | LLRF | - | Intlk | Mon | RA-RaBO01:RF-LLRF:Intlk-Mon | N/A | N/A | RA_RaBO01_RF_LLRF_IntlkMon | Digital | Input |  |  |  | RA_RaBO01_RF_LLRF_IntlkMon | .1
6 | Interlock CLP para o LLRF | BO | 05D | RF | LLRF | - | Intlk | Mon | BO-05D:RF-LLRF:Intlk-Mon | N/A | N/A | BO_05D_RF_LLRF_IntlkMon | Digital | Input |  |  |  | N/A | .1
7 | Termostato Pré-Amp 50 W | RA | RaBO01 | RF | LLRFPreAmp | - | Tms | Mon | RA-RaBO01:RF-LLRFPreAmp:Tms-Mon | N/A | N/A | In | Digital | Input |  |  |  | N/A | .1
8 | PT - 100 01 Pré - Amplificador 50 W | RA | RaBO01 | RF | LLRFPreAmp | - | T1 | Mon | RA-RaBO01:RF-LLRFPreAmp:T1-Mon | RA-RaBO01:RF-LLRFPreAmp:T1UpperLimit-Cte | RA-RaBO01:RF-LLRFPreAmp:T1LowerLimit-Cte | RA_RaBO01_RF_LLRFPreAmp_T1Mon | Analog | Input | Set_Temp[4] |  | C | RA_RaBO01_RF_LLRFPreAmp_T1Mon | .5 | 2
9 | PT - 100 02 Pré - Amplificador 50 W | RA | RaBO01 | RF | LLRFPreAmp | - | T2 | Mon | RA-RaBO01:RF-LLRFPreAmp:T2-Mon | N/A | N/A | RA_RaBO01_RF_LLRFPreAmp_T2Mon | [5 empty] | N/A | .1
10 | Habilita Pré - Amplificador | RA | RaBO01 | RF | LLRFPreAmp | - | Enbl | Mon | RA-RaBO01:RF-LLRFPreAmp:Enbl-Mon | N/A | N/A | RA_RaBO01_RF_LLRFPreAmp_EnblMon | Digital | Output |  |  |  | N/A | .1
11 | PT - 100 01 Pré - Amplificador 50 W acima do set | RA | RaBO01 | RF | LLRFPreAmp | - | T1Up | Mon | RA-RaBO01:RF-LLRFPreAmp:T1Up-Mon | N/A | N/A | RA_RaBO01_RF_LLRFPreAmp_T1UpMon | Digital | Output |  |  |  | RA_RaBO01_RF_LLRFPreAmp_T1UpMon | .1

## Petra 5
Nº | Description | SEC | SUB | DIS | DEV | IDX | PROP | TYPE | NAME | UPPER LIMIT PV NAME | LOWER LIMIT PV NAME | RS Logic | Data Type | In/Out | Upper Limit | Lower Limit | EGU | TAG | Scan | Prec
1 | Interlock Geral Petra V | BO | 05D | RF | P5Cav | - | Sts | Mon | BO-05D:RF-P5Cav:Sts-Mon | N/A | N/A | BO_05D_RF_P5Cav_StsMon | Digital | Control | N/A | N/A |  | BO_05D_RF_P5Cav_StsMon | .1
2 | Petra V Chave de Fluxo 01 | BO | 05D | RF | P5Cav | - | Hd1FlwRt | Mon | BO-05D:RF-P5Cav:Hd1FlwRt-Mon | N/A | N/A | BO_05D_RF_P5Cav_Hd1FlwRtMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Hd1FlwRtMon | .1
3 | Petra V Chave de Fluxo 02 | BO | 05D | RF | P5Cav | - | Hd2FlwRt | Mon | BO-05D:RF-P5Cav:Hd2FlwRt-Mon | N/A | N/A | BO_05D_RF_P5Cav_Hd2FlwRtMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Hd2FlwRtMon | .1
4 | Petra V Chave de Fluxo 03 | BO | 05D | RF | P5Cav | - | Hd3FlwRt | Mon | BO-05D:RF-P5Cav:Hd3FlwRt-Mon | N/A | N/A | BO_05D_RF_P5Cav_Hd3FlwRtMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Hd3FlwRtMon | .1
5 | Petra V PT - 100 Acoplador | BO | 05D | RF | P5Cav | - | CoupT | Mon | BO-05D:RF-P5Cav:CoupT-Mon | BO-05D:RF-P5Cav:CoupTUpperLimit-Cte | BO-05D:RF-P5Cav:CoupTLowerLimit-Cte | BO_05D_RF_P5Cav_CoupTMon | Analog | Input | Set_Temp[7] | Set_Temp[0] | C | BO_05D_RF_P5Cav_CoupTMon | .5 | 2
6 | Petra V PT - 100 Acoplador abaixo do set | BO | 05D | RF | P5Cav | - | CoupTDown | Mon | BO-05D:RF-P5Cav:CoupTDown-Mon | N/A | N/A | BO_05D_RF_P5Cav_CoupTDownMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_CoupTDownMon | .1
7 | Petra V PT - 100 Acoplador acima do set | BO | 05D | RF | P5Cav | - | CoupTUp | Mon | BO-05D:RF-P5Cav:CoupTUp-Mon | N/A | N/A | BO_05D_RF_P5Cav_CoupTUpMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_CoupTUpMon | .1
8 | Petra V Pt - 100 Cilindro 01 | BO | 05D | RF | P5Cav | - | Cylin1T | Mon | BO-05D:RF-P5Cav:Cylin1T-Mon | BO-05D:RF-P5Cav:Cylin1TUpperLimit-Cte | BO-05D:RF-P5Cav:Cylin1TLowerLimit-Cte | BO_05D_RF_P5Cav_Cylin1TMon | Analog | Input | Set_Temp[1] | Set_Temp[0] | C | BO_05D_RF_P5Cav_Cylin1TMon | .5 | 2
9 | Petra V Pt - 100 Cilindro 02 | BO | 05D | RF | P5Cav | - | Cylin2T | Mon | BO-05D:RF-P5Cav:Cylin2T-Mon | BO-05D:RF-P5Cav:Cylin2TUpperLimit-Cte | BO-05D:RF-P5Cav:Cylin2TLowerLimit-Cte | BO_05D_RF_P5Cav_Cylin2TMon | Analog | Input | Set_Temp[1] | Set_Temp[0] | C | BO_05D_RF_P5Cav_Cylin2TMon | .5 | 2
10 | Petra V Pt - 100 Cilindro 03 | BO | 05D | RF | P5Cav | - | Cylin3T | Mon | BO-05D:RF-P5Cav:Cylin3T-Mon | BO-05D:RF-P5Cav:Cylin3TUpperLimit-Cte | BO-05D:RF-P5Cav:Cylin3TLowerLimit-Cte | BO_05D_RF_P5Cav_Cylin3TMon | Analog | Input | Set_Temp[1] | Set_Temp[0] | C | BO_05D_RF_P5Cav_Cylin3TMon | .5 | 2
11 | Petra V Pt - 100 Cilindro 04 | BO | 05D | RF | P5Cav | - | Cylin4T | Mon | BO-05D:RF-P5Cav:Cylin4T-Mon | BO-05D:RF-P5Cav:Cylin4TUpperLimit-Cte | BO-05D:RF-P5Cav:Cylin4TLowerLimit-Cte | BO_05D_RF_P5Cav_Cylin4TMon | Analog | Input | Set_Temp[1] | Set_Temp[0] | C | BO_05D_RF_P5Cav_Cylin4TMon | .5 | 2
12 | Petra V Pt - 100 Cilindro 05 | BO | 05D | RF | P5Cav | - | Cylin5T | Mon | BO-05D:RF-P5Cav:Cylin5T-Mon | BO-05D:RF-P5Cav:Cylin5TUpperLimit-Cte | BO-05D:RF-P5Cav:Cylin5TLowerLimit-Cte | BO_05D_RF_P5Cav_Cylin5TMon | Analog | Input | Set_Temp[1] | Set_Temp[0] | C | BO_05D_RF_P5Cav_Cylin5TMon | .5 | 2
14 | Petra V PT-100 Cilindro 01 abaixo do set | BO | 05D | RF | P5Cav | - | Cylin1TDown | Mon | BO-05D:RF-P5Cav:Cylin1TDown-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin1TDownMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin1TDownMon | .1
15 | Petra V PT-100 Cilindro 01 acima do set | BO | 05D | RF | P5Cav | - | Cylin1TUp | Mon | BO-05D:RF-P5Cav:Cylin1TUp-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin1TUpMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin1TUpMon | .1
16 | Petra V PT-100 Cilindro 02 abaixo do set | BO | 05D | RF | P5Cav | - | Cylin2TDown | Mon | BO-05D:RF-P5Cav:Cylin2TDown-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin2TDownMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin2TDownMon | .1
17 | Petra V PT-100 Cilindro 02 acima do set | BO | 05D | RF | P5Cav | - | Cylin2TUp | Mon | BO-05D:RF-P5Cav:Cylin2TUp-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin2TUpMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin2TUpMon | .1
18 | Petra V PT-100 Cilindro 03 abaixo do set | BO | 05D | RF | P5Cav | - | Cylin3TDown | Mon | BO-05D:RF-P5Cav:Cylin3TDown-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin3TDownMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin3TDownMon | .1
19 | Petra V PT-100 Cilindro 03 acima do set | BO | 05D | RF | P5Cav | - | Cylin3TUp | Mon | BO-05D:RF-P5Cav:Cylin3TUp-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin3TUpMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin3TUpMon | .1
20 | Petra V PT-100 Cilindro 04 abaixo do set | BO | 05D | RF | P5Cav | - | Cylin4TDown | Mon | BO-05D:RF-P5Cav:Cylin4TDown-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin4TDownMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin4TDownMon | .1
21 | Petra V PT-100 Cilindro 04 acima do set | BO | 05D | RF | P5Cav | - | Cylin4TUp | Mon | BO-05D:RF-P5Cav:Cylin4TUp-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin4TUpMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin4TUpMon | .1
22 | Petra V PT-100 Cilindro 05 abaixo do set | BO | 05D | RF | P5Cav | - | Cylin5TDown | Mon | BO-05D:RF-P5Cav:Cylin5TDown-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin5TDownMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin5TDownMon | .1
23 | Petra V PT-100 Cilindro 05 acima do set | BO | 05D | RF | P5Cav | - | Cylin5TUp | Mon | BO-05D:RF-P5Cav:Cylin5TUp-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin5TUpMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin5TUpMon | .1
13 | Petra V Sensor de Pressão | BO | 05D | RF | P5Cav | - | CoupPressure | Mon | BO-05D:RF-P5Cav:CoupPressure-Mon | N/A | N/A | BO_05D_RF_P5Cav_CoupPressureMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_CoupPressureMon | .1
24 | Petra V Termostato Cilindro 01 | BO | 05D | RF | P5Cav | - | Cylin1Tms | Mon | BO-05D:RF-P5Cav:Cylin1Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin1TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin1TmsMon | .1
25 | Petra V Termostato Cilindro 02 | BO | 05D | RF | P5Cav | - | Cylin2Tms | Mon | BO-05D:RF-P5Cav:Cylin2Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin2TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin2TmsMon | .1
26 | Petra V Termostato Cilindro 03 | BO | 05D | RF | P5Cav | - | Cylin3Tms | Mon | BO-05D:RF-P5Cav:Cylin3Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin3TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin3TmsMon | .1
27 | Petra V Termostato Cilindro 04 | BO | 05D | RF | P5Cav | - | Cylin4Tms | Mon | BO-05D:RF-P5Cav:Cylin4Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin4TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin4TmsMon | .1
28 | Petra V Termostato Cilindro 05 | BO | 05D | RF | P5Cav | - | Cylin5Tms | Mon | BO-05D:RF-P5Cav:Cylin5Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Cylin5TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Cylin5TmsMon | .1
29 | Petra V Termostato Disco 01 | BO | 05D | RF | P5Cav | - | Disc1Tms | Mon | BO-05D:RF-P5Cav:Disc1Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Disc1TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Disc1TmsMon | .1
30 | Petra V Termostato Disco 02 | BO | 05D | RF | P5Cav | - | Disc2Tms | Mon | BO-05D:RF-P5Cav:Disc2Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Disc2TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Disc2TmsMon | .1
31 | Petra V Termostato Disco 03 | BO | 05D | RF | P5Cav | - | Disc3Tms | Mon | BO-05D:RF-P5Cav:Disc3Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Disc3TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Disc3TmsMon | .1
32 | Petra V Termostato Disco 04 | BO | 05D | RF | P5Cav | - | Disc4Tms | Mon | BO-05D:RF-P5Cav:Disc4Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Disc4TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Disc4TmsMon | .1
33 | Petra V Termostato Disco 05 | BO | 05D | RF | P5Cav | - | Disc5Tms | Mon | BO-05D:RF-P5Cav:Disc5Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Disc5TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Disc5TmsMon | .1
34 | Petra V Termostato Disco 06 | BO | 05D | RF | P5Cav | - | Disc6Tms | Mon | BO-05D:RF-P5Cav:Disc6Tms-Mon | N/A | N/A | BO_05D_RF_P5Cav_Disc6TmsMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_Disc6TmsMon | .1
35 | Vácuo Petra V | BO | 05D | RF | P5Cav | - | Pressure | Mon | BO-05D:RF-P5Cav:Pressure-Mon | N/A | N/A | BO_05D_RF_P5Cav_PressureMon | Digital | Input | N/A | N/A |  | BO_05D_RF_P5Cav_PressureMon | .1
36 | Potência de RF | BO | 05D | RF | P5Cav | - | PwrRFIntlk | Mon | BO-05D:RF-P5Cav:PwrRFIntlk-Mon | N/A | N/A | BO_05D_RF_P5Cav_PwrRFIntlkMon | Analog | Input | N/A | N/A | dBm | BO_05D_RF_P5Cav_PwrRFIntlkMon | .1 | 4

## Legenda
Variável que tenho dúvida
Variável foi alterada e alteração não foi adicionada no CLP
Variável foi alterada e alteração não foi adicionada no IOC
Variável não existe
Variavel no controlador porém não foi adicionada no CLP